## Slide 1: Maria’s Restaurant Chapter 3 Section 12

## Slide 2: Maria’s Duct Layout Sketch

## Slide 3: Zone 1 Fittings Supply Take Off

## Slide 4: Zone 1 Fittings 4 90s

## Slide 5: Zone 1 Fittings 5 Wye Fittings

## Slide 6: 6 Supply Diffusers & Boxes

## Slide 7: Zone 1 Fittings Return Take Off

## Slide 8: Zone 1 Fittings Return Filter & Grille

## Slide 9: Zone 2 Fittings Supply Take Off

## Slide 10: Zone 2 Fittings Supply 90

## Slide 11: Zone 2 Fittings Supply 5 Wyes

## Slide 12: 6 Supply Diffusers & Boxes

## Slide 13: Manual Q Commercial Low Pressure, Low Velocity Duct System Design

## Slide 14: Duct Pressure Drop Calculation (Typical 90)
H
W
90O
Coefficient C for 90O Duct (Bottom Row) |  |  |  |  |  |  |  |  |  | 
Height ÷ Width (Top Row) |  |  |  |  |  |  |  |  |  | 
0.25 | 0.50 | 0.75 | 1.0 | 1.5 | 2.0 | 3.0 | 4.0 | 5.0 | 6.0 | 8.0
1.3 | 1.3 | 1.2 | 1.2 | 1.1 | 1.1 | 0.98 | 0.92 | 0.89 | 0.85 | 0.83
Reynolds Number Correction (N) | 
CFM | N
50 to 200 | 1.25
200 to 350 | 1.15
350 to 500 | 1.05
Above 500 | 1.00
Adjusted loss Coefficient = C × N | 
90O Rectangular Elbow
CFM = 2,400
H = 24
W = 27
H ÷ W = .8888
CFM ˃ 500
So, N = 1
So, C = 1.2
Velocity Pressure = (Velocity ÷ 4005 × ACF)2
Velocity Pressure = (600 ÷ 4005 × 1)2 = 0.0225
Loss Item
Pt = C × Pv
Pt = 1.2 × 0.0225 = 0.027

## Slide 15: Duct Pressure Drop Calculation (Smooth Radius 3 Vane 90)
Velocity Pressure = (600 ÷ 4005 × 1)2 = 0.0225
Loss Item
Pt = C × Pv
Pt = 0.01 × 0.0225 = 0.000225

## Slide 16: What Does The C Value Difference Mean?
The Pressure Loss is the Coefficient value C multiplied by the velocity pressure (VP) inside of the duct.
Use a VP of 0.359 as an example, to get a total pressure drop across the 90 fitting as the air flows through it. Thus, for the Smooth radius 3 vane 90 the pressure drop would be:
0.01 × 0.359 = 0.00359

## Slide 17: Pressure Drop Value for Standard 90?
Thus, for the standard square 90 with a C value of 1.2, the pressure drop across the fitting would be:
1.2 × 0.359 = 0.43

## Slide 18: Total Pressure Drop Question 1
1.15 × 0.14536 = 0.167164
Use a VP of 0.14536 to get a total pressure drop across the standard square 90 fitting that has a C value of 1.15 as the air flows through it.

## Slide 19: Total Pressure Drop Question 2
1.15 × 0.011362 = 0.0130663
Use a VP of 0.011362 to get a total pressure drop across the standard square 90 fitting that has a C value of 1.15 as the air flows through it.

## Slide 20: Total Pressure Drop Question 3
Use a VP of 0.359 to get a total pressure drop across the 90 fitting as the air flows through it for the standard square 90 with a C value of 1.15. For the Standard Square 90 the pressure drop would be:
1.15 × 0.359 = 0.41285
Note: 0.41285 is called the loss item in Manual Q. It is added to the other loss items to get a total loss for the whole duct run/system

## Slide 21: Question 4 loss Item Total?
Using the loss item totals from Figure 23 on page 52 values for the two shown 90O Ls, find the total loss difference between the two Ls, and which is the more efficient L?
0.0748 – 0.00539 = 0.0694 difference in pressure loss for the two fittings. The smooth radius 3 vain Elbow is by “far and away” the more efficient choice for the duct system.

## Slide 22: Pressure Drop Difference Means What ?
Zone 2 duct design pressure loss totals

## Slide 23: Pressure Drop Difference Means What ?
VP = (518 ÷ 4,005)2 = 0.0167
0.01 × 0.0167 = 0.000167 or 0.0002
a pressure loss item value of 0.0002
The Zone 2 total pressure loss is 0.503

## Slide 24: What Happens If Our Previous Regular 90 Is Put In ?
VP = (518 ÷ 4,005)2 = 0.0167
1.2 × 0.0167 = 0.02004
0.02004 – 0.0002 = 0.01984 + 0.503 = 0.523

## Slide 25: How About Doing The Same 90 Change For Zone 1’s 4 90’s?
Original Chart Values:
Line 8 Loss Item = 0.00359
Line 15 Loss Item = 0.001264
Line 21 Loss Item = 0.000399
Line 25 Loss Item = 0.0000988
Total = 0.00535

## Slide 26: How About Doing The Same 90 Change For Zone 1’s 4 90’s?
Using the chart’s VP values for each line & our
C of 1.20:
Line 8 Loss Item = 0.027
Line 15 Loss Item = 0.022
Line 21 Loss Item = 0.015
Line 25 Loss Item = 0.0108
Total = 0.0748
Total 0.0748 - 0.00535 = 0.06945

## Slide 27: For Zone 1 How Would Blower Motor Size be Changed Due To Changing A Systems Total Pressure Drop from 0.4 to 0.5 ESP?
Looking at Table 12 on Page 46 of the Guide & Workbook:
The motor size would increase.
For example at 1,750 CFM system with an ESP of 0.40 would require a motor with approximately 0.39 Bhp and at 0.50 it would require 0.57 Bhp

## Slide 28: Field Notes
Whenever a duct design is done it is important to make sure the fittings were installed as designed. Often, when a duct system is too small the problem can be resolved by replacing a few standard duct fittings with some higher efficiency ones. It may be as easy as adding some turning vanes to the existing 90s. Redesigning and replacing an entire duct system is a lot more expensive than replacing four or five fittings.