## Slide 1: Lesson 24 Appendix F Outside Air Calculation

## Slide 2: Maria’s Restaurant
Maria’s

## Slide 3
Maria’s Restaurant Design
(Staff: Maria & 6 Employees each shift. Glass Store Front and front door)
66 ft.
25 ft.
F1
R1
S1
DW
C1
CT/O
C2
C3
SP
Fry
R2
F2
Woman’s
Restroom
1 handicap
1 standard
Men’s
Restroom
1 handicap
1 urinal
H1
Bar
Ice
C6
Counter
S3
C7
Bar 12 X 10
Seating 12
Restaurant 33 X 15,
11 X 4 & 11 X 6
Seating 58
R3
R4
B1
Shelv.
S2
SK
Kitchen Area = 533 Sqft Bar Area = 180 Sqft
Woman Rest Room = 110 Sqft Men Rest Room = 99 Sqft
Bar Area = 180 Sqft Entry Area = 120 Sqft
Dinning Area = 605 Sqft
Shelv..
Shelving/Storage
WH
S1
B2

## Slide 4: Restaurant Exhaust and Outside Air
For Maria’s Restaurant, the Restaurant and Bar it
Was decided that Class 2 air from the restaurant area would be used to condition the bathroom areas. Thus, a larger than required exhaust system for the bathrooms was used.

## Slide 5: Operational Outside Air Minimums
Air Classification Definitions from ASHRAE 62.1
Class 1: Air with low contaminant concentration, low
sensory-irritation intensity, and inoffensive odor.
(May be Recirculated to any space.)
Class 2: Air with moderate contaminant concentration,
mild sensory-irritation intensity, or mildly offensive
odors. Class 2 air also includes air that is not necessarily
harmful or objectionable but that is inappropriate for
transfer or recirculation to spaces used for different
purposes.
(Can be recirculated to any space except a class 1 space.)

## Slide 6: Operational Outside Air Minimums
Air Classification Definitions from ASHRAE 62
Class 3: Air with significant contaminant concentration,
significant sensory-irritation intensity, or offensive odor.
(Can only be recirculated in space of origin.)
Class 4: Air with highly objectionable fumes or gases or
with potentially dangerous particles, bioaerosols, or
gases, at concentrations high enough to be considered
harmful.
(Can not be recirculated in space of origin or transferred.)

## Slide 7: ASHRAE 62.1 Outside Air Minimums
Class 2 Air
For a Restaurant or Kitchen 7.5 CFM per person
Air Rate RA CFM/Ft2:
0.12 for Kitchens
0.18 for Restaurants & Bars

## Slide 8: ASHRAE 62.1 Outside Air Minimums
Class 2 Air
For a Restaurant or Kitchen 7.5 CFM per person
Air Rate RA CFM/Ft2:
0.12 for Kitchens
0.18 for Restaurants & Bars
2015 IMC
“403.2.2 Transfer air. Except where recirculation from
such spaces is prohibited by Table 403.3.1.1, air
Transferred from occupiable spaces is not prohibited
from serving as makeup air for required exhaust
systems in such spaces as kitchens, baths, toilet rooms,
elevators and smoking lounges. The amount of transfer
air and exhaust air shall be sufficient to provide the
flow rates as specified in Section 403.3.1.1.”

## Slide 9: 2015 IMC
IMC 403.3.1.1Table: 1 ft3 of air per square foot:
Woman’s Room 110 ft2 X 1 CFM = 110 CFM
Men’s Room 99 ft2 X 1 CFM = 99 CFM
Note: As per design values, 200 CFM per bathroom for ventilation and comfort cooling/heating is transferred from the restaurant area through Jump Ducts.

## Slide 10: 10 ACH (Required by Some Codes)
Woman’s Room 110 ft2 X 8 ft. X 10 = 8,800 CFH
8,800 ÷ 60 = 147 CFM
Men’s Room 99 ft.2 X 8ft. X 10 = 7,920 CFH
7,920 ÷ 60 = 132 CFM
Note: As per design values, 250 CFM per bathroom for ventilation and comfort cooling/heating is transferred from the restaurant area through Jump Ducts.

## Slide 11: ASHRAE 62.1 Outside Air Minimums
Local Code CFM Outside Air Requirement:
Restaurant & Bar Areas Zone 1
Fresh Air Requirement 74 People x 7.5 = 555 CFM
1,117 ft2 Rest. x 0.12 = 134 CFM
Total Fresh Air CFM Required = 689 CFM
Kitchen Area Zone 2
533 ft2 kitchen x 0.18 = 96 CFM
Fresh Air Requirement 3 People x 7.5 = 23 CFM
Total Fresh Air CFM Required = 119 CFM

## Slide 12: ASHRAE 62.1 Outside Air Minimums
Local Code CFM Outside Air Requirement:
Restaurant & Bar Areas Zone 1
Fresh Air Requirement 74 People x 7.5 = 555 CFM
1,117 ft2 Rest. x 0.12 = 134 CFM
Total Fresh Air CFM Required = 689 CFM
Kitchen Area Zone 2
533 ft2 kitchen x 0.18 = 96 CFM
Fresh Air Requirement 3 People x 7.5 = 23 CFM
Total Fresh Air CFM Required = 119 CFM

## Slide 13: ASHRAE 62.1 Outside Air Minimums
Local Code CFM Outside Air Requirement:
Restaurant & Bar Areas Zone 1
Total Fresh Air CFM Required = 689 CFM
Kitchen Area Zone 2
Total Fresh Air CFM Required = 119 CFM
Outside air required for Zone 1 the restaurant side
of the building is 689 CFM: Thus 689 CFM must be
brought into Zone 1 at all times.
Note: (119 CFM into Zone 2)

## Slide 14: Operational Outside Air Minimums
Outside air required for the restaurant side of the
building is 689 CFM: Thus, 689 CFM will be brought
In at all times.
500 CFM will be exhausted through the two
restrooms. That will mean an extra 189 CFM of air
in the restaurant area. This extra air will provide a
slightly positive pressure so, all air leakage from the
Dinning area is into the kitchen or bathroom areas.
Since the restaurant area air is Class 2 this is
allowable.

## Slide 15: Operational Outside Air Minimums
Air Classification Definitions from ASHRAE 62
Food & Beverage Service | Air Classification
Dining Rooms | 2
Cafeteria, fast food | 2
Bars, cocktail lounges | 2
Kitchens (cooking) | 2

## Slide 16: Kitchen Exhaust Requirements Typical Type 1 Exhaust Hood With Perforated Perimeter Supply (11.5 ft. linear length 3,450 CFM hood with 1,150 CFM untempered ASHRAE 62 Class 1 makeup air)

## Slide 17: Kitchen Exhaust Total
Cooking Hood: 3,450 CFM
Dish washer Hood: 600 CFM
Total: 4,050 CFM

## Slide 18: Operational Outside Air Minimums
Outside air required for the kitchen side of the
building by ASHRAE 62.1 is 119 CFM: Thus, 119 CFM
must be brought in at all times.
4,050 CFM will be exhausted through the two
kitchen exhaust hoods. That will leave a negative
3,931 CFM of air if only 119 CFM is brought in from
the outside. Thus, an additional 3,931 CFM of air
will need to be brought into the kitchen if it is to
remain at a neutral pressure with respect to the
outside. (slightly positive to the outside is preferable)

## Slide 19: Kitchen Exhaust & OA Sketch
EX AIR
Speed/Setting 1: 3,450 CFM
Speed/Setting 2: 1,650 CFM
EX 2 AIR
600 CFM
ERV
EX 1
EX 2
2 Bathrooms
Airflow ½ each
EX AIR OUT
500 CFM
EX. AIR
AIR In
500 CFM
AIR In
Setting 1: 1,900 CFM
Setting 2: 100 CFM
Supply Air
3,200 CFM
Return Air
Setting 1: 1,300 CFM
Setting 2: 3,100 CFM
#2 Package Heat Pump
EX. AIR
AIR In
1,150 CFM
AIR In
600 CFM
Bar & Dining Area
(+0.004” IWC)
Kitchen Area
(+0.001” IWC)

## Slide 20: Kitchen Exhaust Total
Cooking Hood: 3,450 CFM
Dish washer Hood: 600 CFM
Total: 4,050 CFM
Bring 1,500 CFM into the hood by a separate outside air fan.
Bring 500 CFM into kitchen area from Bathroom ERV.
The Total CFM Requiring heating and cooling
is Lowered to: 4,050 – 1,400 = 2,650

## Slide 21: ERV Savings for Cooling
An ERV will be used as the exhaust fan in the two bathrooms. The 500 CFM of outside air will be provided to open area over the rear entrance door.
This will save about 2/3 ton of cooling requirement for the required ventilation air.
Note: tonnage savings based on plugging the difference into Manual N calculations for comparison.

## Slide 22: Dining & Bar Exhaust & OA Sketch
ERV
2 Bathrooms
Airflow ½ each
EXHAUST AIR 500 CFM
EXHAUST AIR
500 CFM
AIR In
500 CFM
AIR In 689 CFM
Supply Air
2,400 CFM
# 1 Package Heat Pump
Return Air
1,711 CFM
Bar & Dining Area
(+0.004” IWC)
Kitchen Area
(+0.001” IWC)
AIR In
500 CFM

## Slide 23: ERV

## Slide 24
Separated Air Paths
Through Heat
Transfer Media
Fresh Air
To Building
Building Air
To Outside
Outside Air
To Building
Building Air
To Outside
Filter
Blower
Wheel
Blower
Wheel
500 CFM IN (BLUE) & 500 CFM OUT (Brown)
MERV 8 FILTER

## Slide 25: ERV TRANSFER EFFECIENCY
500 CFM WINTER TOTAL = 70%

## Slide 26: ERV TRANSFER EFFECIENCY
500 CFM SUMMER TOTAL = 60%

## Slide 27: ERV TRANSFER EFFECIENCY
500 CFM SUMMER SENSIBLE = 75%

## Slide 28: ERV LOAD IMPLICATIONS
Winter 500 CFM × 0.70 = 350 CFM
500 – 350 = 150 CFM
Thus, there is an additional 150 CFM of outside air being brought in resulting in slightly less than a 4% increase in total load or 4,290 BTUH

## Slide 29: ERV LOAD IMPLICATIONS
Summer Total Load 500 CFM × 0.60 = 300 CFM
500 – 300 = 200 CFM
Thus, there is an additional 200 CFM of outside air being brought in resulting in slightly less than a 3% increase in total load or 3,268 BTUH

## Slide 30: Makeup Air Fan For Type I Exhaust
The Type I hood selected is designed to have a portion of the outside air come directly into the hood untempered under full operational load. The amount in the design is 1,150 CFM.
This will save a little under 1.5 tons of cooling requirement for the required ventilation air.

## Slide 31: Further Savings: Two Speed Type I Exhaust Hood
The Type I hood selected is designed with an automated control that senses usage. When there is no cooking station usage, hood fan lowers it’s speed so only 1,650 CFM are being exhausted by the hood when the cooking equipment is not being used.
The hood makeup fan’s 1,150 CFM plus the 500 CFM from the ERV then meets the total hood requirement
of 1,650 CFM (1,150 + 500).
This will allow the HVAC system to save over 2 tons of cooling load for the required ventilation air, during off peak operation.

## Slide 32: Field Notes
On many occasions those who know the current outside air code requirements will try to enforce them on existing buildings. Technicians need to find out what the code was when the building was built because the equipment was designed to meet that requirement. Often the equipment is sized so it can not be adjusted to meet a new code requirement. The good news is, if the original code requirement is known, that is what must be met. In simple old fashioned terms: one horse can not pull a two horse load up a hill.