INSTRUCTOR’S LESSON PLAN

For the: TECHNICIAN’S GUIDE & WORKBOOK for Duct Diagnostics and Repairs

Instructors may customize any of the materials in this 4 day course to enhance their student’s learning experience.

This Instructor’s Lesson Plan and all earlier working/review drafts of this lesson plan are protected by copyright.  By making this lesson plan available for use and adoption by public authorities and others, ACCA does not waive any rights in copyright to this lesson plan.  No part of this lesson plan or earlier working/review drafts may be reproduced stored in a retrieval system or transmitted in any form by any technology without permission from ACCA.  Address requests to reproduce, store, or transmit to: ACCA offices in Arlington, Virginia.

©2016, Air Conditioning Contractors of America

2800 Shirlington Road, Suite 300

Arlington, VA   22206

www.acca.org

# Disclaimer and Legal Notice

Diligence has been exercised in the production of this Instructor’s Lesson Plan for the Guide & Workbook.  The content is based on an industry consensus of recognized good practices.  The commentary, discussion, and guidance provided by this publication do not constitute a warranty, guarantee, or endorsement of any concept, observation, recommendation, procedure, process formula, data-set, product, or service.  ACCA and the document reviewers do not warrant or guarantee that the information contained in this publication is free of errors, omissions, misinterpretations, or that it will not be modified or invalidated by additional scrutiny, analysis, or investigation.  The entire risk associated with the use of the information provided by this Guide is assumed by the user.

ACCA does not take any position with respect to the validity of any patent or copyrights rights asserted in connection with any items, process, procedures, or apparatus which are mentioned in or are the subject of this lesson plan, and ACCA disclaims liability of the infringement of any patent resulting from the use of or reliance on this lesson plan.  Users of this lesson plan are expressly advised that determination of the validity of any such patent or copyrights, and the risk of infringement of such rights, is entirely their own responsibility.  Users of this lesson plan should consult applicable federal, state, and local laws and regulations. ACCA does not, by the publication of this lesson plan, intend to urge action that is not in compliance with applicable laws, and this document may not be construed as doing so.  Nothing in this lesson plan should be construed as providing legal advice, and the content is not a substitute for obtaining legal counsel from the reader’s own lawyer in the appropriate jurisdiction or state.

# Table of Contents

# Part 1: Curriculum Outline	1

# Part 2: Answers for Guide & Workbook Q&A Sections	5

# Part 3: Sample Test and Answer Sheet 	12

# Part 4: Other Educational Materials Available 	15

# Introduction

Heating air conditioning and ventilation (HVAC) system performance is evolving and tommorrow’s technicians need far better documentation and technical dignostic capabilities than past generations of technicians.  As the HVAC industry continues to evolve technicians become life long learners in order to keep pace.  Unfortunately, many of today’s technicians have not been trained or equiped to meet today’s requirements.  By, covering the information in this Workbook in detail, you are preparing your students for today’s market. Further, they will be in demand and have many opportunities throughout their careers because they will have the basic understanding and skill set to be successful in the evolving high-tech home performance industry.

This Guide & Workbook was designed as a stand alone course. However, it is recommeneded that students be familiar with duct slide rule usage and ACCA Manual D duct sizing and design basics.

Part 1: Curriculum Outline

This course was developed to support HVAC contractors, home performance professionals, and HVAC instructors who requested more training material on duct diagnostics and repair basics. Contractor participation in editing and adding insight have made this course’s materials industry neutral so they support every home performance certification type.  The curriculum outline is also intended for use by HVAC and Home Performance instructors at vocational-technical schools, training centers, and community colleges; to introduce students to industry-accepted duct diagnostics and repair procedures.

This curriculum has been designed for use with the Technician’s Guide & Workbook for Duct Diagnostics and Repair, a “how-to” “hands-on” guide and workbook. It is designed to be used as a two day intensive classroom course, or may extended to four or more days by adding the recommended hands on exercises.

Course material covers the areas that are commonly taught to technicians in the field. Over 300 power point slides designed for use with the Guide & Workbook are available to instructors from ACCA. They address the requirements for completing a duct inspection and performance analysis, and gathering the information required for improving duct performance.  The instructor may select hands on exercises from recommended options in each section of the Guide & Workbook, or substitute for the hands on exercises with class discussions based on the provided questions designed to encourage class participation.

The outline format allows the instructor to expand or contract the lesson plan to suit the needs of their students, and to augment their available materials, or pre-existing lesson plans. At the end of the two basic 8 hour lessons, a student will understand the requirements for completing a comprehensive duct inspection, analyzing repair requirements, planning repairs, and verifying improved performance.  Finally, the Guide & Workbook contains several appendices designed to be used in the field as reference materials.  For example, ASHRAE 62.2 for determining the make-up/outside air requirements.

Course Materials Needed In Class

- Student Text Book: Technician’s Guide & Workbook for Duct Diagnostics and Repair

Instructor’s Resources

- 2 day, 16 module power point slide presentation designed for 6-8 hour per day lectures (over 300 power point slides available for instructors; ACCA designed for use with the Guide & Workbook)

- Contained in this document, a 16-page Teacher’s Answer Addenda and Guide for questions in the Guide & Work book and recommendations for spicing up the recommended hands on field testing (pages 5-15 )

- Sample self-evaluation final exam answer sheet and exam (pages 12-15)

- Power Point Modules for the Technician’s Guide & Workbook for Duct Diagnostics and repair is available in the free lessons section on ACCA’s Educator’s web page: http://www.acca.org/members/industry/schools

See also, Part 4 of this volume for information on additional ACCA training materials.

Day 1

Part 1 Subjects:

- Airflow in the Building

- Duct Insulation R-Values

- Energy Losses

- Duct Conduction Losses/Gains

- Duct Leakage Losses

Part 2 Subjects:

- Inspecting Duct Systems

- Inspection Factors

- Duct Sketch

Part 3 Subjects:

- Duct System Efficiency Losses

- Duct Damage

- Duct Sizing

- Bad Duct Design Practices

Part 4 Subjects:

- Safety

- Duct Tape

- Duct Repairs

- Planning Duct Repairs

- Considerations For Duct Replacement

Part 5 Subjects:

- ACCA 5 QI Duct Sealing and Testing Requirements

- Insulating Duct Systems

- Correcting Zone Imbalances

Part 6 Subjects:

- Sheet Metal Duct Repairs

- Duct Board Repairs

- Flex-Duct Repairs

- PVC Duct Repairs

Part 7 Subjects:

- Example Of Duct Energy Improvement Through Design

- Jump Duct

- Good Duct Design Practices

Part 8 Subjects:

- Duct Loads

- How Duct Loads Can Change Equipment Sizing

- Duct Loads and Fan Sizing

Day 2

Part 9 Subjects:

- Inspection and Testing Duct

- Duct Static Pressure Testing Tools

- Duct Pressure Testing Tools

- Leakage Testing With Calibrated Fan

Part 10 Subjects:

- Leakage Testing With Airflow Measurement Device

- Leakage Testing With An OEM ESP Chart

- Traversing Duct

- Pressure Differential Testing

- Pressure Pan Testing

Part 11 Subjects:

- Leakage Testing With Flow Grid

- Leakage Testing/Temperature Rise Method

- QI-5 Duct Leakage Testing Requirements

Part 12 Subjects:

- Health Issues

- Safety Issues

Part 13 Subjects:

- Pressurization/Depressurization of Zones

- Furnace Room Depressurization Testing

- Fire Place and Wood Stove Depressurization

- Moisture Issues

- Thermal Comfort Issues

Part 14 Subjects:

- Duct Resistance Diagnostics Story

- Duct Insulation Diagnostics Story

- Duct Temperature Drop Evaluation Story

- Using Duct Static Pressure as a Diagnostic Tool Story

Part 15 Subjects:

- Airflow Measurement Duct Diagnostics Story

- Adjusting Airflow Shortcut Using Fan Laws (Story)

- Thermal Comfort and Drafts

Part 16 Subjects:

- Duct Efficiency

- Thermal Comfort

- Health and Safety

- Golden Opportunities

- Good Design Practice Summary

Part 2: Answer Addenda

Among the questions provided in the Workbook are questions that are designed to encourage class discussion so the instructor can encourage class participation.  The vast majority of the questions are designed to drive home specific important points or to make sure the students find and identify duct leakage or insulation defficiencies that lower HVAC system efficiency. Everything in the Guide & Workbook is part of a usefull knowledge base that is needed in the field today.  By taking the class through the field exercises in the green sections, students will quickly learn what they missed or didn’t fully understand as they try to apply the principles taught.  Additionally, this course is designed to provide students with the knowledge base needed to answer customer questions on existing duct systems.

Answers provided in this Teacher’s Guide are designed to aid instructors when they cover the material in class.  In some cases, additional correct responses may not be identified in this answer guide because there are many possibilities students could come up with.   One additional note:  the author wrote this Guide & Workbook so it could be a tool to be used to create a fun learning experience; so relax, use these questions as a means for interacting with your students, and go with the flow and have some fun!

Test Your Knowledge Study Questions (Page 22)

- What would you recommend to address ducting with a high energy loss related to conduction?

Add insulation (could also write about increasing airflow speed)

- Explain the operating costs associated to duct energy loss:

This is a discussion type of question where students can use the sections to explain why operating cost is higher (25-40%) on a poorly designed, poorly insulated, and poorly installed duct system. The main point is, efficiency improvements save energy and money.

- Explain how air leakage differs in supply and return ducting.

Student answers should focus on how return duct leaking in unoccupied/buffer space causes in occupied space to become positively pressurized vs  the supply duct leaking in unoccupied/buffer space, and as a result, the occupied space to become negatively pressurized vs  outside areas.

- How does zone pressurization affect a room?

The answer should contain an explanation on how positive pressure causes the room to leak to the outside or adjoining rooms.

- How does zone depressurization affect a room?

The answer should contain an explanation on how negative pressure causes the room to pull air in from the adjoining rooms.

- Explain what thermosyphoning is in your own words.

This is designed to make the student explain thermosyphining and not just repeat back what was written in Guide & Workbook. Thus, the answer should contain the important factors like: airflow moves through ducts when the fan is off and it is generally flowing in the wrong direction.

- What indicates there may be duct problems that could lead to health related issues in a building?

More detail for this question is provided in later sections.  In this section, you may expect various answers about added moisture, and exhaust fumes, and allergens being brought in.

- Name some tell-tale signs of duct problems in a building.

Answers come from the section: uninsulated ducts in unconditioned space, disconnected, torn or damaged ducts; abandoned ducts; evidence of leakage; and inadequate supply and or return ducting.

- Explain what needs to be included in a duct drawing or sketch.

This is a good class discussion question. Basically, every part of the duct system should be noted. At a minimum the length, fittings, material type, size, and damaged areas should be noted.

HANDS ON FIELD EXERCISES

- Do a field inspection of a duct system.

Warn them that they will be required to sketch the duct after the field inspection, then let the students examine the duct system and tell you what they see and where.

2.   Do a drawing/sketch of a duct system.

Have them sketch the duct system from memory, and then go back and make corrections and add duct lengths, fittings, and sizes.  This will drive home the point that they need to do this on site.

Test Your Knowledge Study Questions (Page 40)

- Explain why duct tape is never used on sheet metal duct:

Here you can expect some to take exception to the question and write about UL approved tapes. Most will explain why duct tape is unacceptable due to its early failure rate and unacceptability for bonding to duct materials over time.

- Explain what a duct repair should look like:

Basically, the answer is: like the original duct type when it is properly installed.

- Describe conditions that would make duct replacement rather than duct repair necessary.

Expect answers on the condition and or sizing of the duct.

- What would be some advantages of using sheet metal for a new duct installation?

“Sheet metal has two main advantages; the first is the lower friction rate that allows more airflow to pass through a smaller sized duct, the second is durability.”

- What would be some advantages of using duct-board for a new duct installation?

“Fibrous glass duct-board has the advantage of always being insulated, and due to the insulation it absorbs sound.  Thus, providing less of a chance of hearing equipment related noise in the conditioned areas.”

- What would be some advantages of using Flex-duct for a new duct installation?

“The greatest advantage of flexible ducting (flex-duct), as far as efficiency is concerned, is that they don’t leak between ends unless torn.”

- What R-value for duct insulation would you recommend for an unconditioned Florida crawl space?

This will get many answers. Like follow local code. Many should remember Section 1 code specifications and get a value of R-8 for ducts greater than 3” in diameter and R-6 for those smaller than 3” in diameter. However, this could make a good discussion for existing HVAC systems.

- What type of staples should be used to secure duct-board seams?

Outward clinched staples.

- Explain why using openings in the building structure for duct returns is not recommended:

Efficiency, health and duct design should be included in the answers.

- What is a zone imbalance according to this Section?

“Pressure imbalances that depressurize equipment rooms (including rooms containing fireplaces and other room heating devices).”

HANDS ON FIELD EXERCISES

- Do a field repair on a duct system.

This should be done on several types of duct and might include replacing a torn and punctured section of flex duct (students might try repairs).

- Do a field duct leakage test.

This could be done before and after duct repairs are made in the duct.

Test Your Knowledge Study Questions (Page 52)

- Briefly explain what is covered in ASHRAE 62.2 2016.

ASHRAE 62.2 covers the methods for establishing the amount of outside air required in a residence based on size and occupant number.

- Why would a design that separates supply and return outlets by a greater distance be preferable?

Look for citations from the good practices where it is recommended that supplies should be located on inside walls/ceiling areas and returns should be located on outside walls/ceiling areas.

- Explain why duct leakage is a bad thing for a system’s distribution efficiency?

Seasonal distribution efficiencies can be decreased by as much as 44% where 17% of the airflow is leaked out in a poor performing building.  Even where the ducts are in the conditioned space, some rooms may operate hot or cold resulting in an increased energy bill due to the thermostat being adjusted to accommodate the room(s).

- What is a DLF?

Duct Load Factor: Calculated in Manual J using duct area, insulation type, and the temperature of the air inside and outside of the duct (see Manual J section 23 for details).

Duct load factor is the answer to expect. If you teach Manual J it provides a great opportunity for a quick reinforcement!

- What important decision must follow the decision to place duct in unconditioned spaces?

The type of insulation and the R-value and a good duct sealing plan.

- Do design factors differ between residential and commercial low velocity duct systems?

This question might bring in some class conversation since it does not say duct design factors.  However for duct design factors the answer is no.

- Why would a duct system with returns in each room generally increase occupant comfort?

The answer here should include something on the airflow path being completed through the system from the room.

- Why would a duct system with supplies and returns in each room need to be air balanced to provide the design CFM?

All ducted airflow distribution systems should be balanced to make sure the CFM follow in and out of each zone or room is correct.

HANDS ON FIELD EXERCISES

- Do a field drawing and evaluation of an existing duct system.

Note: This should be done on a building with a duct system in need of work when possible. Students can be sent in as a team or as individuals.  The drawings should be compared to see what might be missing.  Go back and point out any parts missed when possible.

- Develop suggestions for design improvements on an existing duct system.

Have the individual students (or as a class) use the drawings to make a repair plan or recommend design improvements for the building’s duct system or portion drawn. For example if there is a section that is not insulated or is damaged or leaking, a repair plan should be developed.  Note: leakage testing before and after could be done on the same duct system as could repairs by the class.  This is most often done on a practice system in a lab to protect the students from falls etc.

Test Your Knowledge Study Questions (Page 73)

- Briefly explain why using a pan joist return duct is not recommended.

Students should by now have this down and should be able to come up with the three main reasons: health concerns, airflow and leakage concerns, and design difficulties.

- For duct leakage tests, why is the AMD subtraction method considered to be less accurate than the CFM25 method?

The answers should include most of the following stuff: Generally the measured values are done in numerous locations and added up for supply and return, then subtracted and compared to the measured fan CFM across system. Box leakage is not considered.  Thus, the CFM25 test is considered as more accurate due to the lack of math and the simple single setup procedure involved (even with its sealing concerns).

- Why it is important to know what orifice ring was used for a calibrated fan duct leakage test?

You can expect all types of answers here from “to make it work” to a long explanation on the Bernoulli principal and the operation of the calibrated fan.

- Name the methods approved in the ANSI/ACCA 5 QI-2015 for measuring fan/furnace airflow.

CFM/Static Pressure (using OEM Tables); traversing the duct; flow grid measurement; pressure matching method, temperature rise method (for heating only applications)

- Why must the duct outlets and inlets be covered prior to doing a CFM25 duct leakage test?

Expect some variation of: To seal the ducts so the leakage can be measured.

- Name the 4 basic steps for duct diagnostics.

Inspect the duct system, test for duct leakage, measure the system airflow rate, and determine what actions to take.

- Explain why the SP pressure difference in the supply and return ducts is important to know when evaluating a CFM25 duct leakage test.

Expect explanations on how the system CFM may be different from the airflow from the CFM25 test due to the system’s operating pressure.

HANDS ON FIELD EXERCISES

- Use at least one of the ANSI/ACCA 5 QI-2015 methods to verify the system’s airflow across the heat exchanger.

It is a better learning exercise when all of the methods can be used and compared.  Additionally, each student should get to try doing the hands on testing procedure. You can put some cardboard on the filter or change some damper positions during a break to liven up the discussion.

- Do a field CFM25 Duct Leakage Test and compare the results to the total system airflow measured.

This test needs to be completely understood by the students. Again, you can poke a hole in, or remove an outlet cover, between student measurements to show why they need to be checked before and after each test.

- Do the AMD Subtraction Method Duct Leakage Test, and compare the results test with Exercise 1.

This is a good way to establish if the students understand the math and the idea that CFM in should equal CFM out for a tight system.

Test Your Knowledge Study Questions (Page 90)

- Name five health and safety issues listed in this guide & Workbook:

Toxins and termiticides from the ground; fumes from stored contaminants; auto exhaust fumes; biological growth; draft spillage; fireplace/stove backdraft; flame rollout; and lack of air change in occupied space.

- Explain what a furnace or water heater backdraft is on a fossil fuel appliance.

Should have answers that say something similar to this: Backdraft is when the vent is bringing air in from the outside.

- Explain why a return duct leaking on HVAC equipment installed in a garage might be unsafe.

It may introduce auto exhaust fumes and other fumes from toxic materials stored in the garage into the occupied space.

- What Remedies would you recommend for a room depressurization caused by a fireplace or wood stove.

Pressurize the room containing the fireplace/wood stove, and/or add outside air pathway for the appliance.

- How could an anemometer be used to solve airflow related comfort issues?

Since anemometers measure airflow in feet per minute, they can be used to identify drafts that are not comfortable to occupants.

- What happens in the 1st floor rooms when there is leakage in return ducts located in the basement?

The airflow returning to the HVAC equipment is lowered. Thus, the circulating CFM is reduced and the 1st floor rooms are positively pressurized and may leak to the outside.

- What happens in the 1st floor rooms when there is leakage in supply ducts located in the basement?

The airflow returning to the HVAC equipment is not changed. However the supply CFM is reduced and the 1st floor rooms are negatively pressurized and may pull air in from the outside.

- What may happen when a room or zone is isolated and has no return pathway?

The airflow returning to the HVAC equipment is lowered. Thus, the circulating CFM is reduced and the isolated room becomes positively pressurized and may leak to the outside.

- How would you make the discharge air temperature in a heat pump more comfortable in the heating mode?

This is a class discussion item.  In the text, it references adding insulation to ducts not in the thermal envelope.  However, making sure the charge is correct, adding an outdoor thermostat for changing over to backup heat etc., may be brought up.

- Why do humidity problems in a building need to be addressed?

Here the answer should include comfort issues, safety issues related to mold growth and moisture related damage issues.

HANDS ON FIELD EXERCISES

- Poll the class on comfort, then measure temperature and humidity in the classroom and place it on the psychrometric chart and compare to comfort zone from figure 80 in this section.

You can add heat or cooling until it seems uncomfortable and do it again if the comfort point is not clear.

Use an anemometer to measure airflow in FPM and locate drafty areas in a building likely to cause some people discomfort.

You can use a fan to make it uncomfortable/drafty in a spot or area and measure the FPM at that location.

Test Your Knowledge Study Questions (Page 99)

- Why are ducted HVAC systems used in most homes built in the U.S?

Cost, performance, and comfort should be mentioned in the answer

- Briefly explain the added operational cost associated when HVAC equipment is not installed correctly.

Here you can expect many answers some more detailed than others, all explaining that it costs more.

- Name 4 thermal comfort problems often reported:

Inadequate cooling or heating capacity, poor humidity control, rooms that are hot or cold (balance or airflow problems), and drafty areas are listed in the text.

- What are the added advantages to improving duct efficiency for heat pump heating applications?

This answer should include: increasing heating air temperature entering into the rooms.

- Name the “4 Golden Opportunities.”

The answers should contain at a minimum the headers:

Comfort, safety, and health enhancements

Improving the performance of heat pumps

Attic ducts in hot humid climates

Duct repair during equipment replacement

- What are 5 things that stop some from placing ducts in the conditioned space?

Difficulty in hiding ductwork

Perceived extra cost

Need for building designer involvement in duct design details

Increased scheduling complications

Lost usable space

- Why should duct systems be designed and not built on the fly?

Main issue they need to hit here is sizing so the duct system will work properly with the delivered CFM at the available ESP.

HANDS ON FIELD EXERCISES

Survey a home or business looking for the” four golden opportunities” and discuss how they would apply to the building.

This can be applied to the sketched systems done in earlier sections or could be an entirely new HVAC system.

- Do a simple payback cost analysis on an HVAC system change out.

Based on the survey of a duct system, use the local energy costs to bring home the point of savings achievable for an old leaking under insulated HVAC system.

Part 3: Sample Test and Answer Sheet

Questions in this test cover every section in the Guide& Workbook.  The weighting for the final grading is up to the instructor.  The original multiple choice quiz was designed to be pass-fail with a 70% cut off for passing.  Because the multiple choice test touches on all of the sections, the results from the multiple choice questions could be used to determine where more time or emphasis is needed for future classes.  Answers below for sample multiple choice test which starts on the next page:

- B

- A

- B

- D

- A

- B

- D

- B

- C

- C

- C

- A

Sample Exam:

- When the return duct located in a vented attic (unconditioned space) leaks, what happens to the buildings internal pressure?

- The building becomes depressurized.

- The building becomes pressurized.

- The building remains at a neutral pressure.

- There is no change to building pressure.

- When the supply duct located in a vented attic (unconditioned space) leaks, what happens to the buildings internal pressure?

- The building becomes depressurized.

- The space becomes pressurized.

- The building remains at a neutral pressure.

- There is no change to building pressure.

- Which of the following not listed as a general consideration in Section 2 of the Technician’s Guide & Workbook for Duct Diagnostics and Repair?

- Health and safety issues.

- “Double-dip” benefits of Using Duct Tape.

- Thermal comfort problems.

- “Double-dip” benefits of Duct Repair.

- Which of the following not listed as a general consideration in Section 2 of the Technician’s Guide & Workbook for Duct Diagnostics and Repair?

- Health and safety issues.

- Low distribution efficiency.

- Thermal comfort problems.

- Duct cleaning issues.

- In Section 3 of the Technician’s Guide & Workbook for Duct Diagnostics and Repair, which of the following is not listed as a component loss (CPL) on the Friction Rate Sheet?

- Duct elbows/90s.

- Humidifier.

- Return grille.

- UV lights or other devices.

- What R-Value below would represent the highest resistance to heat transfer?

- R-2.

- R-14.

- R-8.

- R-11.

- Which of the following is not covered on the visual inspection summary checklist in Section 4 of the Technician’s Guide & Workbook for Duct Diagnostics and Repair?

- Damaged duct.

- Airflow leaking through seams.

- Panned joists.

- Manual D duct design.

- Which of the following is not covered on the visual inspection summary checklist in Section 4 of the Technician’s Guide & Workbook for Duct Diagnostics and Repair?

- Uninsulated duct in unconditioned space.

- Dissimilar duct material usage.

- Rooms where temperatures vary by more than 5o.

- Disconnected duct sections are found.

- Which of the following measurements would meet the furnace room-to-outside pressure difference requirement of being more than -3pa?

- -2pa

- 2pa

- -4pa

- 4pa

- Which of the following statements is not true when the furnace fan is operating and there is a leak in a return duct located in a buffer space (unconditioned linked to the outside)?

- The supply trunk has a strong positive pressure.

- The return trunk has a strong negative pressure.

- The living space will become negatively pressurized

- The living space will become positively pressurized

- Which of the following not listed as one of the 4 “Golden Opportunities”?

- Comfort, Safety, and Health Enhancements.

- Improving the Performance of Heat Pumps.

- More Profit Due to Up-sales.

- Attic Ducts in Warm Humid Climates.

- Which of the following is not listed as one of five difficulties that stand in the way of widespread practice of placing ducts in the conditioned-space?

- Loss in unusable space.

- Perceived extra cost.

- Difficulty in hiding ductwork.

- Need for building designers to become involved with details of duct design.

Part 4: Other Educational Offerings

OVERVIEW: ACCA Training Offerings

ACCA’s Educational Offerings for an Evolving Marketplace

Updated 22 October 2015

As a supplier of educational programs in the HVACR industry for well over 50 years, three factors serve as driving forces within ACCA. First and foremost is to make sure ACCA educational programs and services are of the highest quality; second is to stay a step ahead of the emerging industry needs and trends so that ACCA can offer contractors what they need when they need it, and finally be cost effective in developing and delivering educational programs and services to contractors.  ACCA’s Standards have been widely recognized and accepted by all sectors of the HVAC industry and several have become code requirements.  The chart on the right provides a snapshot view of how ACCA Manuals combine to cover the Design Process.

In advancing its training mission, ACCA avails itself to a number of approaches, from face-to-face training, to video/CD training solutions, to the online certificate program, to webinars, to ensuring its manuals/standards/guides are on the cutting edge of industry good practices, to develop educational plot forms for A) Contractors, B) Technicians, C) Consumers, D) Instructors, and E) Code Officials [see attached sheets for specifics on each].

FACE-TO-FACE TECHNICAL EDUCATION (‘Classroom Setting’)

(For more information, contact www.acca.org, or call 703-575-4477)

- Residential Design For Quality Installations (RDQI):  A journeyman or higher level, three-day course covering Residential Design for Quality Installations includes: Manual J8® (Load Calculations), Manual D® (Duct Design), and the ANSI/ACCA 5-QI-2014 (HVAC Quality Installation Specification). Also included are: Manual T® (Air Distribution Basics), Manual S® (Equipment Selection), and ACCA’s Duct Slide Rule, that provides the students with all of the tools needed to properly design and supervise the installation of an HVAC system to meet code as well as Energy Star® requirements.

- Educational Program Instructor Certification (EPIC):  Residential EPIC is a master or expert level course that covers the residential design process in depth and requires the use of a Windows-based lap top computer.  Material provided and covered includes the following: Manual J8® (load Calculations), Manual S® (Equipment Selection), Manual D® (Duct Design), Manual H® (Heat Pump Systems), Manual P® (Psychrometrics), Manual T® (Air Distribution Basics), Manual TT-102® Understanding the Friction Chart), and Manual 4® (Perimeter Heating and Cooling).

Commercial EPIC parallels the residential EPIC course covering ACCA’s commercial design materials: Manual CS® (Commercial Applications, Systems and Equipment), Manual N® (Commercial Load Calculation), Manual H® (Heat Pump Systems), Manual P® (Psychrometrics), Manual T® (Air Distribution Basics), and Manual Q® (Commercial Low Pressure, Low Velocity, and Duct System Design)

- Seminars at ACCA meetings, conferences, and councils: ACCA’s continues to evolve its seminar classroom opportunities that are made available in conjunction with various meetings and other events.  These draw a large number of people where it is cost-effective to offer multiple learning modules:

  - ACCA Conference and IE3 Indoor Air EXPO.

  - Building Performance Forum (a two-day learning experience for contractors co-sponsored by ACCA and BPI).

  - National HVACR Service Managers Forum (a two-day learning experience exclusively for service managers in contracting businesses).

  - Commercial Contracting Roundtable (the leading educational and networking experience for commercial HVACR contractors).

  - Numerous sessions provided at monthly local ACCA chapter meetings.

INDIVIDUALIZED STUDY

Embracing what ACCA sees as an important part in the education of the future, ACCA has developed individualized training so it can be used when and where the user wants.  Individualized study materials are available in several formats designed to meet individual needs: CDs, Videos, recorded webinars, and Manuals/Guides. ACCA’s material provides high quality training and reusable training materials at an affordable price so contractors can train employees when it is convenient.

- Quality Assurance Accreditation Programs: ACCA now offers an online training course with testing that allow contractors to receive accreditation for the Energy Star New Homes program (QA), ACCA’s Existing Homes –Residential Service & Installation (RSI), and the RSI Verifier Program.

- Energy and Home Performance Programs: ACCA offers online training courses with testing that allow contractors to become program members.  The programs include the Quality Assured (QA) program and the Residential Service & Installation (RSI) program.

- Webinars for ACCA Members: ACCA provides members with access to the latest business practices and technology implementations through webinars.  Webinars are seen as a hybrid methodology that allows those who want to participate to have access to very specific topics when it is more convenient for them.

- QTech Online Training (CEU) Programs: ACCA offers online 6 hour video QI and QH training courses with a pdf copy of the selected guide & workbook and online testing that allows a technician to receive a certificate that is recognized for CEUs by BPI, ESCO, NATE, RESNET, and RSES.

INDUSTRY TRAINING COLLABORATIONS

- North America Technician Excellence (NATE):  ACCA is committed to NATE certification as a mark of distinction and a way for consumers and contractors to gain a true comfort level with the professionalism of HVAC technicians.

- Instructor Workshops: ACCA has been working with the Council of Air Conditioning and Refrigeration Educators (CARE), and to develop and disseminate the information HVACR instructors want and need.

- Building Performance Forum: ACCA forum for HVAC contractors and raters involved in the home performance industry held in conjunction with the Building Performance Institute, Inc. (BPI).

ACCA values collaborative partnerships with business entities and allied associations to advance the goal of quality education in a cost effective manner.

Contractor: ACCA Training Offerings

ACCA’s Educational Offerings for an Evolving Marketplace

Updated 4 November 2015

Contractor To Contractor

For access to member benefits:	 http://members.acca.org/home

- ACCA Conference

- Mixed Groups

- Code of Professional Conduct

- ACCA Blogs

- Federal Affairs

- State Affairs

- Conference & Expo

- Industry News & Opinion

- Service Managers Forum

- Building Performance

QA & RSI Training

Access to all contractors:

http://www.acca.org/qa/resources

- QA Contractor Elements

- Participation Requirements

- Outdoor Load Calculation Design Conditions

- QA Sample Policy Template

- ENERGY STAR Checklists

- RSI HVAC Verifiers

Free To Members Video Training

Watch: http://members.acca.org/acca/watch

- Performance Reviews For Success

- Stress in Service Contracting

- 10 Easy Steps to Handling the Poor Performer

Plus, ACCA has an additional 133 additional Videos covering contracting management and employee relationship issues.

Safety Downloads

Risk Management Library:	 http://www.acca.org/members/downloads

- A SIR Program – It’s Just the Ticket!

- Who Are You Insuring?

- Who Pays for Errors?

- Conduct a “Safety” Interview

- Don’t Risk a Lot to Save a Little

- Distracted Driving: At What Cost?

- First Impressions Work Both Ways

- Set Driving Expectations

- Workers’ Compensation Fraud

- How Much Is a Good Name Worth?

- Two to Hire, Two to Fire!

- Preparing for a Flu Pandemic

- Concentrate On Safety

- Real Value or Paper Value?

- Winter Driving Woes

- Battling Mother Nature

- Business Interruption

- Add TLC to Workers’ Comp

- Back to Back Safety

Free Member Downloads

Keeping contractors up to date:

http://members.acca.org/home

- Residential HVAC Design for Quality Installation (Jack Rise Course)

- Technical Bulletins

- Customizable Brochures

- Comfor Tools (to be customized for distribution to customers)

- Q&A Section

- Forms and Templates

- ACCA Annual Report

- Hurricane Last Minute Essentials Guide

- Sample Emergency Management Plan

- Open for Business Planning Package

Contractor Focused CD’s & DVDs

Training Library:

http://www.hvacessentials.com

- Contractor Soft Skills DVD

- Convert Phone Calls into More Sales DVD

- LEED, Follow or Get Out of the Way (Book and/or CD)

Forums & Annual Meeting

Live Training & Information:	 http://members.acca.org/home

- ACCA Conference & IE3 Expo

- Service Manager Forum

- Building Performance Forum

- Radiant & Hydronic Forum

Free To Members Audio Training

Listen: http://members.acca.org/acca/listen/

- The Price Is Right! How To Properly Price Commercial Services

- The Next Generation of HVAC

- Private Label Products: Are They Worth It?

Plus, 30 Additional Audio Programs addressing business related issues.

Political Action Committee

Legislation Tracking, Grassroots Action Center and Federal affairs updates on the following items brings the latest information on in following areas of interest to contractors:

http://www.capwiz.com/acca/home/

- Tax Legislation

- Regional standards

- Copper & Metal Theft

- Healthcare

- Labor

- Commercial Energy Eff. Incentives

- Residential Energy Eff. Incentives

- Refrigerants

- Regional Standards

- Regulatory reform

- Small Business Capital Investment

- Transportation

Breaking News

IE3 Media: http://www.ie3media.com/

- IE3

- Insider Emails

- Special Interest Council News Letters:

- Building Performance

- Radiant and Hydronics

ACCA Town Hall

Town hall discussions and issues discussed.

http://www.acca.org/members/videos

Why Join ACCA?

To become part of the leading edge in the HVACR industry and grow your business.

Learn what ACCA has to offer Contractors: http://www.acca.org/join/

- Free Training

- Free Technical & Legal Support

- Free Downloads

- Connect with:

- Customers

- Contractors

- Job Seekers

Technician: ACCA Training Offerings

ACCA’s Educational Offerings for an Evolving Marketplace

Updated 4 November 2015

Video and CD Training

ACCA on line store: www.acca.org/store

HVAC Essentials

- Understanding Manual J: Heat Gain & Heat Loss in the Real World

- Understanding Manual D: Airflow & Duct Design in the Real World

- Understanding Section 608: refrigerant Handling in the Real World

- Understanding Manual N: Commercial Load Calculation in the Real World

- Understanding Quality Installation

- Understanding Electricity

- Understanding Manual Q: Low Pressure, Low Velocity Duct Design in the Real World

- Understanding Manual Zr

- HVAC Essentials Understanding 608

- Tips for Residential HVAC Installation CD

- Control System Basics for HVAC Technicians CD

- Refrigeration and Air Conditioning 7th Edition CD set

Nate Training CDs

- Mastering Core Service CD

- Mastering Heat Pump Service CD

- Mastering Core Installation CD

- Mastering Air Conditioning Inst. CD

- NATE Air Conditioning and Heat Pumps CD

- NATE Air Distribution CD

- NATE Gas and Oil Heating CD

- NATE Hydronics CD

Mobile App

https://www.calcunow.com

Duct Wheel for iPad

Qtech Online Course CEU’s

Available at: http://www.acca.org

- Quality Installation

- NATE Essentials

- Understanding Section 608

- Technician’s Guide & Workbook for Quality installations

- Technician’s Guide & Workbook for Home Performance  Improvements

Training Books and Materials

ACCA on line store: www.acca.org/store

- Study Guide for EPA Section 608 (English, Spanish, and Italian)

- Training Manual for EPA Section 608 (English, and Spanish)

- Section 608 Refresher Manual (English, and Spanish)

- EPA 609 Certification and Training Manual

- Calculator/Pocket Card Set

- Careers In the HVAC Industry

- Control System Basics for HVAC Technicians

- Customer Service Handbook For HVACR Technicians

- Airflow In Ducts

- Blueprints and Plans For HVAC

- Commercial System Quick Reference (CSQR)

- Digital Controls for HVAC Technicians

- Duct Calculation Slide Rule

- Energy Efficiency Manual

- Fans and V-Belt Drives

- Geothermal HVAC: Green Heating and Cooling

- Good HVAC Practices for Residential and Commercial Buildings (ACCA)

- Green Guide

- HVAC Equations, Data, and Rules of thumb, 2nd Edition

- HVAC Licensing Study Guide

- HVAC Spanish

- Math for the Technician

- Refrigeration and Air Conditioning 7th

- Modern Refrigeration and Air Conditioning, 19th Edition

- Refrigeration for HVAC Technicians How Refrigeration Works

- Troubleshooting HVAC-R Equipment

- Building Science Principles Reference Guide

- Geothermal HP Training Manual

- Tech to Tech

- How Come?

- Modern Hydronic Heating

- Pumping Away, and other really cool piping options for hydronic system

- Residential Hydronic Heating, Installation and Design

- The Lost Art of Steam Heating

- Refrigeration for HVAC Technicians

- Bob’s House

- Duct Diagnostics and Repair

- HVAC Installation Procedures Handbook

- HVAC Maintenance Procedures Handbook

- HVAC Service Procedures Handbook

- Layout for Duct Fittings

- Manual 4 Inst. Techniques for Perimeter heating and Cooling

- Tips for Residential HVAC Inst.

- HVAC Servicing Procedures Handbook

- HVAC Installation Procedures Handbook

- HVAC Maintenance Procedures Handbook

- Installing Residential Forced Air Furnaces

- Layout For Duct Fittings

NATE Training Manuals

ACCA on line store: www.acca.org/store

- NATE A/C & Heat Pumps Manual

- NATE Air Distribution

- NATE Essentials Manual

- NATE Gas and Oil Heating

- NATE Hydronics

- Mastering Air Distribution Service

- Mastering Hydronics – Gas Service

- Mastering Gas Furnace installation

- Mastering Gas Furnace Service

- NATE Core Essentials

- NATE Air Conditioning and Heat Pumps

- NATE Air Distribution

- NATE Gas and Oil Heating

- NATE Hydronics

Course Related Text and Work Books

ACCA online store: www.acca.org/store

- Technician’s Guide & Workbook for QI

- Manual B Balancing and Testing Air and Hydronic Systems

- Manual H Heat Pump Systems and Applications

- Controls – Level 1 Fundamentals

- Life Cycle Costing for HVAC SYS.

- Principles of Mechanical Refrigeration

Consumer: ACCA Training Offerings

ACCA’s Educational Offerings for an Evolving Marketplace

Updated 4 November, 2015

ACCA develops innovative consumer education materials for light commercial and residential customers.  Tools are designed to help consumers locate and evaluate HVACR contractors. They help consumers recognize contractors who have differentiated themselves by offering standards-based quality installation services. Extensive web information on how to:

- Find a contractor

- Select a contractor

- What questions to ask a contractor

- What the QI is

- Contractor proposal evaluation checklists

- Commonly asked questions and answers

- Texts that explain basic HVAC design and installation principles in non-technical language

Consumer Videos

Animated Videos:

- Comfort Health Safety  http://www.acca.org/homes/

- When Is The Best Time To Ask These Questions? http://www.acca.org/homes/

Videos:

- A Guide For Home Heating and Air Conditioning http://www.acca.org/homes/

- A Guide For Business Heating AND Air Conditioning Services  http://www.acca.org/buildings/

Consumer Checklists

Quality Installation Checklist (English & Spanish) http://www.acca.org/homes/

Quality Maintenance Checklist (Residential and Commercial Versions) http://www.acca.org/homes/

Frequently Asked Questions & The Right Questions To Ask

Found at: http://www.acca.org/homes/

- Are your technicians NATE certified? NATE certification is the industry’s standard for technician excellence. You should never accept anything less.

- Do you offer continuing education to your employees? This industry changes rapidly. Ask the contractor to describe their training program.

- Can you provide local references? Get the names of neighbors who have used the company’s services, and then follow up with them.

- Do you offer a service agreement plan? Well-maintained equipment runs more efficiently and lasts longer.

- Are you properly licensed? Unfortunately, every state, city, or county could have different contractor licensing rules. Ask for proof!

- Do you follow the industry standards? Make sure your contractor knows what “Manual J” and “Quality Installation” are, just for a start. Scroll down on this page to find out what these standards are and why they are important to you!

Texts Designed For End Users

Found at: http://www.acca.org/store

Bob’s House, a case study for understanding the residential HVAC design process and Manual RS- Comfort, Air Quality, & Efficiency by Design are designed to be used by those who want a basic understanding of HVAC design practices.

Instructor: ACCA Training Offerings

ACCA’s Educational Offerings for an Evolving Marketplace

Updated 4 November 2015

ACCA participates in HVACR Instructor Work Shops and develops education materials for light commercial and residential training.  ACCA helps instructors provide the training that contractors need today’s technicians to have.  The net result of using ACCA’s HVACR training materials is to provide students with market place skills based on the HVACR industry’s good practices and procedures.

Free Downloads From The ACCA Website

Manual N Speedsheet video              Manual Jae Speedsheet video                     QI Standards

Speedsheet Videos available at: www.acca.org/speedsheet

Other Supporting Resource Materials Available as Free Downloads:

Standards available at: www.acca.org/standards/quality :

- HVAC Quality Installation Specification (English)

- HVAC Quality Installation Specification (Spanish)

- Home Performance Evaluation & Improvement

- HVAC Quality Installation Protocols

- Quality Maintenance of Residential HVAC Systems

- HVAC System Cleanliness & Restoration

ACCA Instructor’s Lesson Plans

ACCA has lesson plans for Instructors available on the educator’s page on the website. Lesson plans are available for:

- EDU 1-9/2015 Instructor’s Lesson Plan for Manuals J, D, and S.

- EDU 2-9/2015 Instructor’s Lesson Plan for Technician’s Guide & Workbook for Quality Installations

- EDU 3-9/2015 Instructor’s Lesson Plan for Technician’s Guide & Workbook for Home Performance Improvement

North American Technical Excellence Instructor’s CDs

NATE CDs available at: www.acca.org/store

- NATE A/C & Heat Pumps Manual

- NATE Air Distribution

- NATE Essentials Manual

- NATE Gas and Oil Heating

- NATE Hydronics

Instructor Power Point Presentations on CD’s

Cd’s developed for Instructor Use In the Classroom

Power points available at: www.acca.org/store

- Controls – Level 1 Fundamentals

- Life Cycle Costing for HVAC Systems

- Principles of Mechanical Refrigeration

- Simutech –Simuair- Air Conditioning Simulator Training System

- Water Piping and Heat Pumps- Instructor

- Residential Design Instructor Power point

- Commercial design Instructor Power Point

- 608 Certification Program  (Refrigerant Transition and recovery Certification Instructor Manual includes lesson plans and overhead masters) Procter Sign Up: http://www.acca.org/for-contractors/

- Understanding Section 608

ACCA’s Educational Program Instructor Certification (EPIC)

ACCA’s Educational Program Instructor Certification (EPIC) is a 4 day course designed for those instructors with a master’s level experience in HVAC systems. Participants must supply their own windows-based computer system.  The following Manuals and materials are provided by ACCA:

Residential EPIC available at: www.acca.org/education/epic/

- Manual D (Duct Design)

- Manual J (Load Calculation)

- Manual H (Heat Pump Systems)

- Manual P (Psychrometrics)

- Manual S (Equipment Selection)

- Manual T (Air Distribution Basics)

- Manual 4 (Perimeter Heating & Cooling)

- Manual TT-102 (Understanding the Friction Chart)

Apprenticeship Program

ACCA developed a training series of Manuals designed to teach what contractors need entry level technicians to know.  Designed to be a two or four year program, the books are available with an Instructor’s Guide CD.  The following Courses are designed to build upon one another:

- HVACR 101 Book and Instructor’s Guide on CD

- HVACR 201 Book and Instructor’s Guide on CD

- HVACR 301 Book and Instructor’s Guide on CD

- HVACR 401 Book and Instructor’s Guide on CD

Available at: www.acca.org/store

Instructor’s Training Certification Manual

ACCA has a Geothermal Heat Pump Training Certification Instructor Manual available for those who wish to teach the basics of Geothermal Heat Pump design and installations.  Available at: www.acca.org/store

Code Officials: ACCA Training & Resources

ACCA’s Educational Offerings for an Evolving Marketplace

Updated 4 November, 2015

ACCA develops education materials for light commercial and residential Code Officials.  Tools are designed to help them understand the basic requirements for HVACR designs.  Additionally, ACCA is available as a trusted unbiased HVACR industry expert to answer Code Official’s questions one on one when they call in.

Building Code Requirements for ACCA Manuals

The following national codes make reference to specific ACCA procedures in order to comply. Jurisdictions that adopt these codes require the use of ACCA procedures as outlined in our technical manuals.

- The IAPMO’s Uniform Mechanical Code requires the use of Manual J (Residential Load Calculation), Manual N (Commercial Load Calculation), Manual D (Residential Duct Systems), and Manual Q (Commercial Duct Systems).

- The ICC’s International Mechanical Code requires the use of Manual D (Residential Duct Systems).

- The ICC’s International Residential Code requires the use of Manual J (Residential Load Calculation) and Manual S (Residential Equipment Selection), Manual D (Residential Duct Systems).

- The ICC’s International Energy Conservation Code requires the use of Manual J (Residential Load Calculation) and Manual S (Residential Equipment Selection).

Codes Verification Brochure’s for Manuals J, D, and S

Available at: http://www.acca.org/standards/codes/

Videos for Code Officials

Available at:  https://www.acca.org/standards/codes/

Residential System Design Review Forms

Available at:  https://www.acca.org/standards/codes/

Illustrated examples and review form downloads are made available for free to Code Officials

- ICC Residential System Review Form

- UMC Residential System Review Form

- Understanding & Using the System Review Form

Bob’s House

A Manual designed to walk Code Officials through the whole design process on a typical home.

Guidance on Approved Software Meeting Code Requirements

A brochure designed to provide guidance on approved software providers http://www.acca.org/standards/software/