## Slide 1: Maria’s Restaurant Lesson 21 Appendix C Duct Design

## Slide 2
Maria’s Restaurant Design
(Staff: Maria & 7 Employees each shift. Glass Store Front and front door)
66 ft.
25 ft.
F1
R1
S1
DW
C1
CT/O
C2
C3
SP
Fry
R2
F2
Woman’s
Restroom
1 handicap
1 standard
Men’s
Restroom
1 handicap
1 urinal
H1
Bar
Ice
C6
Counter
S3
C7
Bar 12 X 10
Seating 12
Restaurant 33 X 15
11 X 4 & 11 X 6
Seating 58
R3
R4
B1
Shelv.
S2
SK
B = Beverage Area R = Refrigerator (blue walk in
C = Counter S = Sink; S1 Hand; S2 3 Pot; S3 Bar
CT = 4 burner plus flat top over ovens SK= Steam Kettle
DW = Dishwasher SP = Salad/cold Prep table
F = Freezer (blue walk in) H1 = Hot Prep Table with Heat Lamp Shelf
Shelv..
Shelving/Storage
WH
S1
B2

## Slide 3: Dining & Bar Exhaust & OA Sketch
ERV
2 Bathrooms
Airflow ½ each
EX AIR OUT
500 CFM
EX. AIR
AIR In
500 CFM
AIR In 689 CFM
Supply Air
2,400 CFM
# 1 Package Heat Pump
Return Air
1,711 CFM
Bar & Dining Area
(+0.004” IWC)
Kitchen Area
(+0.001” IWC)

## Slide 4
Maria’s Restaurant Duct Layout
(one grid square = one ft2)
66 ft.
25 ft.
Zone 1
EX. Hood
Zone 2
Zone 2 Constant Volume 3,200 CFM
Stage 1 Return: 1,300 CFM
Stage 2 Return: 3,100 CFM
Zone 1
Supply Diffuser 550 CFM
5 Supply Diffusers 530 CFM Each
6 Supply Diffusers 400 CFM Each
Zone 1 Constant Volume 2,400 CFM
Return: 1,711 CFM
A
B
C
F
D
E
G
H
A
B
C
D
E
G
F
H

## Slide 5
Maria’s Restaurant Duct Layout
(one grid square = one ft2)
66 ft.
25 ft.
Zone 1 Duct
EX. Hood
Zone 2
Zone 2 Constant Volume 3,200 CFM
Stage 1 Return: 1,300 CFM
Stage 2 Return: 3,100 CFM
Zone 1
Supply Diffuser 550 CFM
5 Supply Diffusers 530 CFM Each
6 Supply Diffusers 400 CFM Each
Zone 1 Constant Volume 2,400 CFM
Return: 1,711 CFM
A
B
C
F
D
E
G
H
A
B
C
D
E
G
F
H

## Slide 6
24”
27”
27”
24”
Fan Cabinet Return Connections for 7.5 & 10 Ton Rooftop Package Unit Supply Duct
26” Round
Friction Rate (FR) Calculation
Zone 1 Unit Return Trunk: 2,400 CFM ÷ 4.5 ft2 = 534 FPM
FR = 0.016 (Will use 0.020 as per Manual Q Minimum value)
Zone 2 Unit Return Trunk: 3,200 CFM ÷ 4.5 ft2 = 711 FPM
FR = 0.030
Note: Sketch not to scale
27”× 24” = OEM Opening

## Slide 7
Maria’s Restaurant Duct Design
(one grid square = one ft2)
66 ft.
25 ft.
Zone 1A
Duct
EX. Hood
Zone 2
Zone 1
6 Supply Diffusers 400 CFM
Zone 1 Constant Volume 2,400 CFM
Return: 1,711 CFM
A
B
C
D
E
G
F
H
Not a significant Pressure Drop:
For longer runs or smaller ducting
the return total needs to be added
to the supply to obtain the system’s
total loss.

## Slide 8
20”
28”
28”
20”
Friction Rate (FR) Calculation
Zone 1 Unit Supply Trunk: 2,400 CFM ÷ 3.89 ft2 = 617 FPM
FR = 0.0208
Zone 2 Unit Supply Trunk: 3,200 CFM ÷ 3.89 ft2 = 823 FPM
FR = 0.045
Note: Sketch not to scale
Fan Cabinet Supply Connections for 7.5 & 10 Ton Rooftop Package Unit Supply Duct
26” Round
28”× 20” = OEM Opening
Not a significant Pressure Drop:
For longer runs or smaller ducting
the return total needs to be added
to the supply to obtain the system’s
total loss.

## Slide 9
Zone 1 Duct Design
(one grid square = one ft2)
66 ft.
25 ft.
Zone 1A
Duct
EX. Hood
Zone 2
Zone 1
6 Supply Diffusers 400 CFM
Zone 1 Constant Volume 2,400 CFM
Return: 1,711 CFM
A
B
C
D
E
G
F
H
Diffuser
90O Rectangular Elbow
Wye 90

## Slide 10: A to B
A-B
Outside Air Damper
Drop Across The Filter
Drop Across The Coil
Inlet = 0 (from return)
Outlet = 0 (design)

## Slide 11
OEM DATA For 7.5 Ton Zone 1 Rooftop Package Unit

## Slide 12: B to C
Duct Size
24 H × 27 W
7 ft
15 ft

## Slide 13: B to C Straight Duct 24” × 27”
Loss Item
CE = f/100 × ft. ÷ 100
CE = 0.02 × 15 ÷ 100 = 0.003
CE = 0.02 × 7 ÷ 100 = 0.0014

## Slide 14: B to C 90 Bend From Q A6-1
H
W
90O
Coefficient C for 90O Duct (Bottom Row) |  |  |  |  |  |  |  |  |  | 
Height ÷ Width (Top Row) |  |  |  |  |  |  |  |  |  | 
0.25 | 0.50 | 0.75 | 1.0 | 1.5 | 2.0 | 3.0 | 4.0 | 5.0 | 6.0 | 8.0
1.3 | 1.3 | 1.2 | 1.2 | 1.1 | 1.1 | 0.98 | 0.92 | 0.89 | 0.85 | 0.83
Reynolds Number Correction (N) | 
CFM | N
50 to 200 | 1.25
200 to 350 | 1.15
350 to 500 | 1.05
Above 500 | 1.00
Adjusted loss Coefficient = C × N | 
90O Rectangular Elbow
CFM = 2400
H = 24
W = 27
H ÷ W = .8888
CFM ˃ 500
So, N = 1
So, C = 1.2

## Slide 15: L 90 Mitered Rectangle Calculation
Loss Item
Pt = C × Pv
Pt = 1.2 × 0.359 = 0.4309
Velocity Pressure = (Velocity ÷ 4005 × ACF)2
Velocity Pressure = (2,400 ÷ 4005 × 1)2 = 0.359

## Slide 16: Smooth Radius 3 Vane 90 #1
H/W = 0.8889
R/W = 0.5
R/W | Coefficient C |  |  |  |  |  |  |  |  |  | 
 | H/W |  |  |  |  |  |  |  |  |  | 
 | 0.25 | 0.5 | 1.0 | 1.5 | 2.0 | 3.0 | 4.0 | 5.0 | 6.0 | 7.0 | 8.0
0.05 | 0.11 | 0.10 | 0.12 | 0.13 | 0.14 | 0.16 | 0.18 | 0.19 | 0.21 | 0.22 | 0.23
0.10 | 0.07 | 0.05 | 0.06 | 0.06 | 0.06 | 0.07 | 0.07 | 0.08 | 0.08 | 0.08 | 0.09
0.15 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.05 | 0.05
0.20 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
0.25 | 0.03 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
0.30 | 0.03 | 0.02 | 0.02 | 0.02 | 0.02 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
0.35 | 0.02 | 0.02 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
0.40 | 0.02 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
0.45 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
0.50 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
No need to interpolate C = 0.01

## Slide 17: Smooth Radius 3 Vane 90 #1
Velocity Pressure = (Velocity ÷ 4005 × ACF)2
Velocity Pressure = (2,400 ÷ 4005 × 1)2 = 0.359
Loss Item
Pt = C × Pv
Pt = 0.01 × 0.359 = 0.00359

## Slide 18: Savings for 4 Smooth Radius 3 Vane 90

## Slide 19: Smooth Radius 3 Vane 90
# 2 H/W = 0.8
# 2 R/W = 0.5
R/W | Coefficient C |  |  |  |  |  |  |  |  |  | 
 | H/W |  |  |  |  |  |  |  |  |  | 
 | 0.25 | 0.5 | 1.0 | 1.5 | 2.0 | 3.0 | 4.0 | 5.0 | 6.0 | 7.0 | 8.0
0.05 | 0.11 | 0.10 | 0.12 | 0.13 | 0.14 | 0.16 | 0.18 | 0.19 | 0.21 | 0.22 | 0.23
0.10 | 0.07 | 0.05 | 0.06 | 0.06 | 0.06 | 0.07 | 0.07 | 0.08 | 0.08 | 0.08 | 0.09
0.15 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.05 | 0.05
0.20 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
0.25 | 0.03 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
0.30 | 0.03 | 0.02 | 0.02 | 0.02 | 0.02 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
0.35 | 0.02 | 0.02 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
0.40 | 0.02 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
0.45 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
0.50 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
No need to interpolate C = 0.01

## Slide 20: Smooth Radius 3 Vane 90 # 3
# 3 H/W = 0.4
# 3 R/W = 0.5
R/W | Coefficient C |  |  |  |  |  |  |  |  |  | 
 | H/W |  |  |  |  |  |  |  |  |  | 
 | 0.25 | 0.5 | 1.0 | 1.5 | 2.0 | 3.0 | 4.0 | 5.0 | 6.0 | 7.0 | 8.0
0.05 | 0.11 | 0.10 | 0.12 | 0.13 | 0.14 | 0.16 | 0.18 | 0.19 | 0.21 | 0.22 | 0.23
0.10 | 0.07 | 0.05 | 0.06 | 0.06 | 0.06 | 0.07 | 0.07 | 0.08 | 0.08 | 0.08 | 0.09
0.15 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.05 | 0.05
0.20 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
0.25 | 0.03 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
0.30 | 0.03 | 0.02 | 0.02 | 0.02 | 0.02 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
0.35 | 0.02 | 0.02 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
0.40 | 0.02 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
0.45 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
0.50 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
No need to interpolate C = 0.01

## Slide 21: Smooth Radius 3 Vane 90 # 4
# 4 H/W = 0.28
# 4 R/W = 0.5
R/W | Coefficient C |  |  |  |  |  |  |  |  |  | 
 | H/W |  |  |  |  |  |  |  |  |  | 
 | 0.25 | 0.5 | 1.0 | 1.5 | 2.0 | 3.0 | 4.0 | 5.0 | 6.0 | 7.0 | 8.0
0.05 | 0.11 | 0.10 | 0.12 | 0.13 | 0.14 | 0.16 | 0.18 | 0.19 | 0.21 | 0.22 | 0.23
0.10 | 0.07 | 0.05 | 0.06 | 0.06 | 0.06 | 0.07 | 0.07 | 0.08 | 0.08 | 0.08 | 0.09
0.15 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.05 | 0.05
0.20 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
0.25 | 0.03 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
0.30 | 0.03 | 0.02 | 0.02 | 0.02 | 0.02 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
0.35 | 0.02 | 0.02 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
0.40 | 0.02 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
0.45 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
0.50 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
No need to interpolate C = 0.01

## Slide 22: SP TOTAL For 4 90s In Zone 1
VS
Loss Item
#1 = 0.4309
#2 = 0.15168
#3 = 0.0509
#4 = 0.0022
Total = 0.63568
Loss Item
#1 = 0.00359
#2 = 0.0013
#3 = 0.0004
#4 = 0.0001
Total = 0.00539

## Slide 23: Duct Design From C to H
4 ft
3 ft
6 ft
11 ft
11 ft
5 ft
14 ft
9 ft

## Slide 24: Zone 1 Wye C Rectangular (Pv)
Using the Manual Q Table A6-5
to Calculate for main Coefficient
C at point C on the duct drawing:
Ab ÷ Ac = 175 ÷ 648 = 0.27
Ab ÷ As = 175 ÷ 500 = 0.35
Qb ÷ Qc = 400 ÷ 2,400 = 0.167
Where:
Ab = 7 × 25 = 175 in2
Ac = 24 × 27 = 648 in2
As = 20 × 25 = 500 in2

## Slide 25: Main Branch Wye C Rectangular (Pv) (Table from Manual Q: A 6-1)
Ab/As | Ab/Ac | Wye Main Branch Coefficient C |  |  |  |  |  |  |  | 
 |  | Qb/Qc |  |  |  |  |  |  |  | 
 |  | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9
0.25 | 0.25 | -0.01 | -0.03 | -0.01 | 0.05 | 0.13 | 0.21 | 0.29 | 0.38 | 0.46
0.33 | 0.25 | 0.08 | 0 | -0.02 | -0.01 | 0.02 | 0.08 | 0.16 | 0.24 | 0.34
0.5 | 0.5 | -0.03 | -0.06 | -0.05 | 0 | 0.06 | 0.12 | 0.19 | 0.27 | 0.35
0.67 | 0.5 | 0.04 | -.02 | -0.04 | -0.03 | -0.01 | 0.04 | 0.12 | 0.23 | 0.37
1.0 | 0.5 | 0.72 | 0.48 | 0.28 | 0.13 | 0.05 | 0.04 | 0.09 | 0.18 | 0.30
1.0 | 1.0 | -0.02 | -0.04 | -0.04 | -0.01 | 0.06 | 0.13 | 0.22 | 0.30 | 0.38
1.33 | 1.0 | 0.10 | 0 | 0.01 | -0.03 | -0.01 | 0.03 | 0.10 | 0.20 | 0.30
2.0 | 1.0 | 0.62 | 0.38 | 0.23 | 0.13 | 0.08 | 0.05 | 0.06 | 0.10 | 0.20
Ab ÷ Ac = 175 ÷ 648 = 0.27
Ab ÷ As = 175 ÷ 500 = 0.35
Qb ÷ Qc = 400 + 2,400 = 0.167
Qb/Qc
Interpolate for 1.7 Between
0.08 and 0 = about 0.02

## Slide 26: Main Branch 1st Wye Rectangular (Pv) (Table from Manual Q: A 6-1)
Ab/As | Ab/Ac | Wye Main Branch Coefficient C |  |  |  |  |  |  |  | 
 |  | Qb/Qc |  |  |  |  |  |  |  | 
 |  | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9
0.25 | 0.25 | -0.01 | -0.03 | -0.01 | 0.05 | 0.13 | 0.21 | 0.29 | 0.38 | 0.46
0.33 | 0.25 | 0.08 | 0 | -0.02 | -0.01 | 0.02 | 0.08 | 0.16 | 0.24 | 0.34
0.5 | 0.5 | -0.03 | -0.06 | -0.05 | 0 | 0.06 | 0.12 | 0.19 | 0.27 | 0.35
0.67 | 0.5 | 0.04 | -.02 | -0.04 | -0.03 | -0.01 | 0.04 | 0.12 | 0.23 | 0.37
1.0 | 0.5 | 0.72 | 0.48 | 0.28 | 0.13 | 0.05 | 0.04 | 0.09 | 0.18 | 0.30
1.0 | 1.0 | -0.02 | -0.04 | -0.04 | -0.01 | 0.06 | 0.13 | 0.22 | 0.30 | 0.38
1.33 | 1.0 | 0.10 | 0 | 0.01 | -0.03 | -0.01 | 0.03 | 0.10 | 0.20 | 0.30
2.0 | 1.0 | 0.62 | 0.38 | 0.23 | 0.13 | 0.08 | 0.05 | 0.06 | 0.10 | 0.20
Ab ÷ Ac = 175 ÷ 648 = 0.27
Ab ÷ As = 175 ÷ 500 = 0.35
Qb ÷ Qc = 400 + 2,400 = 0.167
Qb/Qc
Interpolate for 1.7 Between
0.08 and 0 = about 0.02
0.02
0.17
- 0.045
Close Enough to 0

## Slide 27: Wye C In Table
Velocity Pressure = (Velocity ÷ 4005 × ACF)2
Velocity Pressure = (2,000 ÷ 4005 × 1)2 = 0.249376
Loss Item
Pt = C × Pv
Pt = 0 × 0.2494 = 0

## Slide 28: Zone 1 Wye D Rectangular (Pv)
Using the Manual Q Table A6-5
to Calculate for main Coefficient
C at point C on the duct drawing:
Ab ÷ Ac = 175 ÷ 500 = 0.35
Ab ÷ As = 175 ÷ 450 = 0.39
Qb ÷ Qc = 400 ÷ 2,000 = 0.2
Where:
Ab = 7 × 25 = 175 in2
Ac = 20 × 25 = 500 in2
As = 18 × 25 = 450 in2

## Slide 29: Main Branch Wye D Rectangular (Pv)
Ab/As | Ab/Ac | Wye Main Branch Coefficient C |  |  |  |  |  |  |  | 
 |  | Qb/Qc |  |  |  |  |  |  |  | 
 |  | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9
0.25 | 0.25 | -0.01 | -0.03 | -0.01 | 0.05 | 0.13 | 0.21 | 0.29 | 0.38 | 0.46
0.33 | 0.25 | 0.08 | 0 | -0.02 | -0.01 | 0.02 | 0.08 | 0.16 | 0.24 | 0.34
0.5 | 0.5 | -0.03 | -0.06 | -0.05 | 0 | 0.06 | 0.12 | 0.19 | 0.27 | 0.35
0.67 | 0.5 | 0.04 | -.02 | -0.04 | -0.03 | -0.01 | 0.04 | 0.12 | 0.23 | 0.37
1.0 | 0.5 | 0.72 | 0.48 | 0.28 | 0.13 | 0.05 | 0.04 | 0.09 | 0.18 | 0.30
1.0 | 1.0 | -0.02 | -0.04 | -0.04 | -0.01 | 0.06 | 0.13 | 0.22 | 0.30 | 0.38
1.33 | 1.0 | 0.10 | 0 | 0.01 | -0.03 | -0.01 | 0.03 | 0.10 | 0.20 | 0.30
2.0 | 1.0 | 0.62 | 0.38 | 0.23 | 0.13 | 0.08 | 0.05 | 0.06 | 0.10 | 0.20
Ab ÷ Ac = 175 ÷ 500 = 0.35
Ab ÷ As = 175 ÷ 450 = 0.39
Qb ÷ Qc = 400 ÷ 2,000 = 0.2
Close Enough to 0

## Slide 30: Zone 1 Wye E Rectangular (Pv)
Using the Manual Q Table A6-5
to Calculate for main Coefficient
C at point C on the duct drawing:
Ab ÷ Ac = 175 ÷ 450 = 0.39
Ab ÷ As = 175 ÷ 425 = 0.41
Qb ÷ Qc = 400 ÷ 1,600 = 0.25
Where:
Ab = 7 × 25 = 175 in2
Ac = 18 × 25 = 450 in2
As = 17 × 25 = 425 in2

## Slide 31: Main Branch Wye E Rectangular (Pv)
Ab/As | Ab/Ac | Wye Main Branch Coefficient C |  |  |  |  |  |  |  | 
 |  | Qb/Qc |  |  |  |  |  |  |  | 
 |  | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9
0.25 | 0.25 | -0.01 | -0.03 | -0.01 | 0.05 | 0.13 | 0.21 | 0.29 | 0.38 | 0.46
0.33 | 0.25 | 0.08 | 0 | -0.02 | -0.01 | 0.02 | 0.08 | 0.16 | 0.24 | 0.34
0.5 | 0.5 | -0.03 | -0.06 | -0.05 | 0 | 0.06 | 0.12 | 0.19 | 0.27 | 0.35
0.67 | 0.5 | 0.04 | -.02 | -0.04 | -0.03 | -0.01 | 0.04 | 0.12 | 0.23 | 0.37
1.0 | 0.5 | 0.72 | 0.48 | 0.28 | 0.13 | 0.05 | 0.04 | 0.09 | 0.18 | 0.30
1.0 | 1.0 | -0.02 | -0.04 | -0.04 | -0.01 | 0.06 | 0.13 | 0.22 | 0.30 | 0.38
1.33 | 1.0 | 0.10 | 0 | 0.01 | -0.03 | -0.01 | 0.03 | 0.10 | 0.20 | 0.30
2.0 | 1.0 | 0.62 | 0.38 | 0.23 | 0.13 | 0.08 | 0.05 | 0.06 | 0.10 | 0.20
Ab ÷ Ac = 175 ÷ 450 = 0.39
Ab ÷ As = 175 ÷ 425 = 0.41
Qb ÷ Qc = 400 ÷ 1,600 = 0.25
Close Enough to 0
0.25

## Slide 32: Zone 1 Wye F Rectangular (Pv)
Using the Manual Q Table A6-5
to Calculate for main Coefficient
C at point C on the duct drawing:
Ab ÷ Ac = 175 ÷ 425 = 0.41
Ab ÷ As = 175 ÷ 250 = 0.7
Qb ÷ Qc = 400 ÷ 1,200 = 0.333
Where:
Ab = 7 × 25 = 175 in2
Ac = 17 × 25 = 425 in2
As = 10 × 25 = 250 in2

## Slide 33: Main Branch Wye F Rectangular (Pv)
Ab/As | Ab/Ac | Wye Main Branch Coefficient C |  |  |  |  |  |  |  | 
 |  | Qb/Qc |  |  |  |  |  |  |  | 
 |  | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9
0.25 | 0.25 | -0.01 | -0.03 | -0.01 | 0.05 | 0.13 | 0.21 | 0.29 | 0.38 | 0.46
0.33 | 0.25 | 0.08 | 0 | -0.02 | -0.01 | 0.02 | 0.08 | 0.16 | 0.24 | 0.34
0.5 | 0.5 | -0.03 | -0.06 | -0.05 | 0 | 0.06 | 0.12 | 0.19 | 0.27 | 0.35
0.67 | 0.5 | 0.04 | -.02 | -0.04 | -0.03 | -0.01 | 0.04 | 0.12 | 0.23 | 0.37
1.0 | 0.5 | 0.72 | 0.48 | 0.28 | 0.13 | 0.05 | 0.04 | 0.09 | 0.18 | 0.30
1.0 | 1.0 | -0.02 | -0.04 | -0.04 | -0.01 | 0.06 | 0.13 | 0.22 | 0.30 | 0.38
1.33 | 1.0 | 0.10 | 0 | 0.01 | -0.03 | -0.01 | 0.03 | 0.10 | 0.20 | 0.30
2.0 | 1.0 | 0.62 | 0.38 | 0.23 | 0.13 | 0.08 | 0.05 | 0.06 | 0.10 | 0.20
Ab ÷ Ac = 175 ÷ 425 = 0.41
Ab ÷ As = 175 ÷ 250 = 0.7
Qb ÷ Qc = 400 ÷ 1,200 = 0.333
Close Enough to 0
0.41

## Slide 34: Zone 1 Wye G Rectangular (Pv)
Using the Manual Q Table A6-5
to Calculate for main Coefficient
C at point C on the duct drawing:
Ab ÷ Ac = 175 ÷ 250 = 0.7
Ab ÷ As = 175 ÷ 175 = 1
Qb ÷ Qc = 400 ÷ 8,00 = 0..5
Where:
Ab = 7 × 25 = 175 in2
Ac = 10 × 25 = 250 in2
As = 7 × 25 = 175 in2

## Slide 35: Main Branch Wye F Rectangular (Pv)
Ab/As | Ab/Ac | Wye Main Branch Coefficient C |  |  |  |  |  |  |  | 
 |  | Qb/Qc |  |  |  |  |  |  |  | 
 |  | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9
0.25 | 0.25 | -0.01 | -0.03 | -0.01 | 0.05 | 0.13 | 0.21 | 0.29 | 0.38 | 0.46
0.33 | 0.25 | 0.08 | 0 | -0.02 | -0.01 | 0.02 | 0.08 | 0.16 | 0.24 | 0.34
0.5 | 0.5 | -0.03 | -0.06 | -0.05 | 0 | 0.06 | 0.12 | 0.19 | 0.27 | 0.35
0.67 | 0.5 | 0.04 | -.02 | -0.04 | -0.03 | -0.01 | 0.04 | 0.12 | 0.23 | 0.37
1.0 | 0.5 | 0.72 | 0.48 | 0.28 | 0.13 | 0.05 | 0.04 | 0.09 | 0.18 | 0.30
1.0 | 1.0 | -0.02 | -0.04 | -0.04 | -0.01 | 0.06 | 0.13 | 0.22 | 0.30 | 0.38
1.33 | 1.0 | 0.10 | 0 | 0.01 | -0.03 | -0.01 | 0.03 | 0.10 | 0.20 | 0.30
2.0 | 1.0 | 0.62 | 0.38 | 0.23 | 0.13 | 0.08 | 0.05 | 0.06 | 0.10 | 0.20
Ab ÷ Ac = 175 ÷ 250 = 0.7
Ab ÷ As = 175 ÷ 175 = 1
Qb ÷ Qc = 400 ÷ 800 = 0.5
Close to .055
Velocity Pressure = (Velocity ÷ 4005 × ACF)2
Velocity Pressure = (400 ÷ 4005 × 1)2 = 0.01
Loss Item
Pt = C × Pv
Pt = 0.01 × 0.055 = 0.0006

## Slide 36: Zone 1 Wye G Rectangular (Pv)
Using the Manual Q Table A6-5
to Calculate for main Coefficient
C at point C on the duct drawing:
Ab ÷ Ac = 175 ÷ 250 = 0.7
Ab ÷ As = 175 ÷ 175 = 1
Qb ÷ Qc = 400 ÷ 1,200 = 0.333
Where:
Ab = 7 × 25 = 175 in2
Ac = 10 × 25 = 250 in2
As = 7 × 25 = 175 in2

## Slide 37: Zone 1 Wye G Rectangular (Pv)

## Slide 38: Zone 1 H Diffuser
TABLE 13: XYZ Commercial Square Diffuser (Throw X = Throw Y) |  |  |  |  |  |  |  |  |  |  | 
Face Velocity |  | 500 | 600 | 700 | 800 | 900 | 1,000 | 1,200 | 1,400 | 1,600 | 1,800
Pressure Loss |  | 0.020 | 0.020 | 0.030 | 0.040 | 0.050 | 0.060 | 0.090 | 0.120 | 0.160 | 0.200
6×6 Ak .10 | CFM Throw | 50 2-3 | 60 2-3 | 70 2-4 | 80 2-4 | 90 3-5 | 100 3-5 | 120 4-6 | 140 4-8 | 160 4-8 | 180 5-9
9×9 Ak .22 | CFM Throw | 110 3-5 | 135 2-4 | 155 3-5 | 180 3-5 | 205 4-6 | 270 5-9 | 270 5-9 | 315 6-11 | 360 6-12 | 410 7-13
12×12 Ak .40 | CFM Throw | 200 3-5 | 240 4-6 | 280 4-8 | 320 5-8 | 360 5-9 | 480 6-12 | 480 6-12 | 560 7-13 | 640 8-15 | 725 9-17
15×15 Ak .62 | CFM Throw | 310 4-6 | 375 4-8 | 440 5-9 | 500 6-11 | 565 6-11 | 750 8-15 | 750 8-15 | 875 10-18 | 1,000 10-19 | 1,125 12-21
18×18 Ak .90 | CFM Throw | 450 4-8 | 540 5-9 | 630 5-11 | 720 6-12 | 810 7-13 | 1,080 10-17 | 1,080 10-17 | 1,260 11-20 | 1,440 13-23 | 1,620 15-27
21×21 Ak 1.23 | CFM Throw | 615 5-9 | 740 6-11 | 860 7-13 | 985 8-14 | 1,110 9-15 | 1,475 11-21 | 1,475 11-21 | 1,725 13-25 | 1,970 15-29 | 2,220 17-31
24×24 Ak 1.60 | CFM Throw | 800 5-11 | 960 7-13 | 1,120 7-14 | 1,275 8-15 | 1,440 9-17 | 1,925 12-23 | 1,925 12-23 | 2,240 14-29 | 2,570 16-31 | 2,890 18-35
27×27 Ak 2.02 | CFM Throw | 1,010 6-12 | 1,010 6-12 | 1,420 8-15 | 1,615 10-18 | 1,820 10-19 | 2,020 12-22 | 2,430 14-27 | 2,840 16-32 | 3,240 18-35 | 3,650 20-38
33×33 Ak 2.75 | CFM Throw | 1,370 7-13 | 1,370 7-13 | 1,925 10-18 | 2,200 21-21 | 2,470 14-24 | 2,750 16-27 | 3,300 18-33 | 3,850 19-37 | 4,400 23-41 | 4,950 27-46
Noise Criterion |  | NC ˂ 30 |  | NC 30 |  | NC 35 |  | NC 40 |  | NC ≥ 40 | 
Note: Minimum throw based on a terminal velocity of 200 fpm; Maximum throw based on a terminal velocity of 100 fpm. |  |  |  |  |  |  |  |  |  |  | 
650
400
0.25

## Slide 39: Zone 1 Total Loss
Total Loss = 0.514
Note, without upgraded 90s
and with standard Ts and 90Oreducers
The Total loss would have been 1.167

## Slide 40: Zone 1 Motor Size
Air Volume CFM | 0.20 |  | 0.40 |  | 0.60 |  | 1.0 |  | 1.60 |  | 2.00 |  | 2.60 | 
 | RPM | Bhp | RPM | Bhp | RPM | Bhp | RPM | Bhp | RPM | Bhp | RPM | Bhp | RPM | Bhp
1,750 | 460 | 0.19 | 548 | 0.39 | 618 | 0.57 | 758 | 0.81 | 941 | 1.23 | 1039 | 1.55 | 1156 | 2.08
2,000 | 492 | 0.27 | 560 | 0.47 | 629 | 0.64 | 768 | 0.88 | 946 | 1.32 | 1041 | 1.65 | 1160 | 2.13
2,250 | 505 | 0.35 | 573 | 0.55 | 643 | 0.72 | 780 | 0.97 | 952 | 1.42 | 1044 | 1.76 | 1164 | 2.27
2,500 | 520 | 0.45 | 588 | 0.64 | 658 | 0.81 | 793 | 1.07 | 959 | 1.54 | 1048 | 1.89 | 1166 | 2.42
2,750 | 536 | 0.55 | 604 | 0.74 | 674 | 0.91 | 806 | 1.19 | 968 | 1.67 | 1053 | 2.04 | 1167 | 2.60
3,000 | 553 | 0.66 | 622 | 0.85 | 692 | 1.02 | 821 | 1.32 | 977 | 1.83 | 1059 | 2.21 | 1170 | 2.79
3,250 | 572 | 0.77 | 641 | 0.98 | 712 | 1.15 | 837 | 1.48 | 988 | 2.00 | 1066 | 2.41 | 1174 | 3.01
3,500 | 592 | 0.90 | 663 | 1.12 | 733 | 1.31 | 854 | 1.65 | 999 | 2.19 | 1074 | 2.63 | 1180 | 3.24
2,400 CFM
.514
1.167
A “Total Loss” Difference Between 0.514 and 1.165
approximately doubles the horsepower required to
move the same 2,400 CFM

## Slide 41
20”
28”
28”
20”
Friction Rate (FR) Calculation
Zone 1 Unit Supply Trunk: 2,400 CFM ÷ 3.89 ft2 = 617 FPM
FR = 0.0208
Zone 2 Unit Supply Trunk: 3,200 CFM ÷ 3.89 ft2 = 823 FPM
FR = 0.045
Note: Sketch not to scale
26” Round

## Slide 42
24”
27”
27”
24”
26” Round
Friction Rate (FR) Calculation
Zone 1 Unit Supply Trunk: 2,400 CFM ÷ 4.5 ft2 = 534 FPM
FR = 0.016 (Will use 0.020 as per Manual Q Minimum value)
Zone 2 Unit Supply Trunk: 3,200 CFM ÷ 4.5 ft2 = 711 FPM
FR = 0.030
Note: Sketch not to scale

## Slide 43
Vc
(Fpm)
Vs
(Fpm out)
Ac
(Area in)
As
(Area out)
Ab
(Area Branch)
Vb
(Fpm Branch)
R
W
R
W
=
1
W) Wye, Rectangular
(upstream Pv)
R ÷ W = 1
90O Branch
FPM | Branch | Trunk
900 | 0.03 | 0.00
1,500 | 0.07 | 0.01
2,100 | 0.14 | 0.02
Loss (Pt)

## Slide 44
Maria’s Restaurant Duct Layout
(one grid square = one ft2)
66 ft.
25 ft.
Zone 1
EX. Hood
Zone 2
Zone 2 Constant Volume 3,200 CFM
Stage 1 Return: 1,300 CFM
Stage 2 Return: 3,100 CFM
Zone 1
Supply Diffuser 550 CFM
5 Supply Diffusers 530 CFM Each
6 Supply Diffusers 400 CFM Each
Zone 1 Constant Volume 2,400 CFM
Return: 1,711 CFM
A
B
C
F
D
E
G
H
A
B
C
D
E
G
F
H

## Slide 45: Field Notes
Duct designs are just that…designs. They are nice to have if there is a duct related problem like a high equipment ESP, coils icing up in cooling, heat going down on the heat exchanger’s high temperature safety, etc. Often the design can not be followed and an installer will put in what seems to fit rather than size the replacement/changed section. Top technicians should be able to find where the restrictions are by measuring static pressure at points in the duct system. For more on this see Technician’s Guide & Workbook for Duct Diagnostics and Repair or the Qtech course on same.