## Slide 1: Maria’s Restaurant Chapter 2 Section 7

## Slide 2: Equipment Selection Process
For Heating: For Cooling:
Forced Air Forced Air
Fossil fuel furnaces (gas or oil) Electric Air Conditioner
Stoves burning wood or fuel pellets Air source heat pump
Air source heat pump Evaporative Cooler (Swamp cooler)
Electric furnace or resistance heat Geothermal or water source heat pump
Geothermal or water source heat pump Chilled water
Variable refrigerant flow Variable Refrigerant Flow
Hydronic Heat Hydronic Cooling
Boiler (hot water or steam heat) Radiant
Geothermal or water source heat pump Chilled Beam
Electric water heater
Fossil fuel water heater

## Slide 3: Three Basic Design Factors
Cooling coil airflow – Generally expressed in these blower speed intervals:
  Low - High,
  Low – Medium – High,
  Low – Medium Low - Medium High - High.
  Variable
Outdoor air temperature – This is the temperature of the air around the outdoor condensing coil, sometimes called the condenser air temperature. (Keep in mind this temperature may not exactly match what is listed on the manufacturer’s data, so we may have to interpolate.)
Condition of air entering the indoor coil – OEMs use either a dry bulb temperature, a wet bulb temperature, or may ask for some dry bulb – wet bulb combination.

## Slide 4: Cooling Design Information

## Slide 5: Heating Design

## Slide 6: Zone 2 Total Load

## Slide 7: Manual N Zone 2 Heating Load
107,764 Btuh Total Heating Load
(With ERV Load added)

## Slide 8: Zone 2 Heating Data Sheet
Zone 2 Heating 10 Ton Unit
Design Load 107,764
High Heat Rating 115,000
Low Heat Rating 70,000
115,000 ÷ 107,764 × 100 = 107%
70,000 ÷ 107,764 × 100 = 65%

## Slide 9: Zone 2 Manual N Cooling Load
96,495 Btuh Sensible Cooling Load
19,039 Btuh Latent Cooling Load
115,534 Btuh Total Cooling Load

## Slide 10: Zone 2 Manual N Cooling Load In Tons
115,534 ÷ 12,000 = 9.63

## Slide 11: Zone 2 Cooling Data Sheets
Zone 2 Cooling 10 Ton Unit
Design Load 115,534
Gross Load Rating 121,000
Net Load Rating 118,000
121,000 ÷ 115,534 × 100 = 105%
118,000 ÷ 115,534 × 100 = 102%

## Slide 12: But Wait!
AHRI tests and publishes information pertaining to the “data plate” seasonal efficiency of electric air conditioners and heat pumps. The AHRI published efficiency and capacity ratings are based on the following special set conditions:
The unit is tested at 400 CFM per ton
The outdoor dry bulb (DB) temperature is 95°F
The DB temperature of the air entering the cooling coil is 80°F
The indoor/entering wet bulb5 (EWB) temperature is 67°F (equivalent to 80°F DB and 50% Rh).

## Slide 13: Expanded Data For “10 Ton” Equipment
88OF

## Slide 14: Expanded Data For “10 Ton” Equipment
88OF
Our interpolated value for our 88OF design location would be 124.9 kBtuh

## Slide 15: Expanded Data For “10 Ton” Equipment
88OF
At full capacity, our sensible cooling ÷ total cooling = 0.67
so, 0.67 × 124,900 Btuh = sensible heat = 83,683 Btuh.
Thus, the latent cooling capacity must be 124,900 – 83,683 = 41,217 Btuh.

## Slide 16: Manual CS Cooling Requirements OK
Thus, the selected unit will meet our design requirements for cooling.
124,900 ÷ 115,534 × 100 = 108% of the design value for total cooling.
The latent heat value of 41,217 Btuh exceeds the design value of 19,039 Btuh so it passes too.
Manual CS recommends selecting unit less than 115% of the load calculation where, the sensible capacity exceeds the sensible load and the latent value exceeds the latent load.

## Slide 17: Zone 2 Manual N Heating Load
105,820 Btuh
At 3,200 CFM: interpolating between 45 OF and 25 OF; a total heating capacity of 106,250
100.4% of the design….OK, it works on heat pump alone for heating

## Slide 18: Interpolation 1
Using the chart above interpolate for the KBtuh value for an entering wet bulb temperature of 63OF and 4,000 CFM at 90OF

## Slide 19: Interpolation 1
Easy Interpolation because it is at the midpoint between 85OF and 95 OF. Thus the two values can be added and divided by 2.
(124.8 + 116.4) ÷ 2 = 120.6 kBtuh

## Slide 20: Interpolation 2
Using the chart above interpolate for the KBtuh value for an entering wet bulb temperature of 67OF and 4,000 CFM at 87OF

## Slide 21: Interpolation 2
Step 1: Temperature Total Difference: 95OF - 85 OF = 10
Step 2: Temperature Ratio Factor: 95 – 87 = 8
Step 3: Temperature Ratio: 8 ÷ 10 = 0.8
Step 4: kBtuh total Difference: 133.2 – 124 = 9.2
Step 5: Temperature Ratio × kBtuh Total = 0.8 × 9.2 = 7.36
Step 6: 124 + 7.36 = 131.36 kBtuh

## Slide 22: Interpolation 3
Using the chart above interpolate for the KBtuh value for an entering wet bulb temperature of 67OF and 4,800 CFM at 92OF

## Slide 23: Interpolation 3
Step 1: Temperature Total Difference: 95OF - 85 OF = 10
Step 2: Temperature Ratio Factor: 95 – 92 = 3
Step 3: Temperature Ratio: 3 ÷ 10 = 0.3
Step 4: kBtuh total Difference: 137.8 – 128.3 = 9.5
Step 5: Temperature Ratio × kBtuh Total = 0.3 × 9.5 = 2.85
Step 6: 128.3 + 2.85 = 131.15 kBtuh

## Slide 24: Field Notes
Two common mistakes found in the field are equipment that was sized based on the rated load values not the expanded values and equipment installed, started up and left running right like it came out of the box.
Only technician’s that can look at the expanded data, and then set up a system to run at the correct CFM can make a system run as designed.
Note: Sometimes the only way it can meet the latent cooling load requirements.