## Slide 1: Maria’s Restaurant Chapter 3 Section 13

## Slide 2: Supply & Return Damper Pressure Drops

## Slide 3: Airflow Calculations & Duct Sizing
You want to avoid having to order a new set of pulleys, new belts and a larger motor at every start up. It is easy to avoid that circle dance by always totaling the pressure drops for every duct design done on a slide rule. Unfortunately, this is rarely done by those who use a duct slide rule to do design ducts. They size the sections one at a time, cross their fingers, and hope for the best. In a worst case situation, they could burn up the blower motor during its initial startup.

## Slide 4: Rule Of Thumb Again
For duct designs, as usual, rules-of-thumb should be ignored, 8” duct does not mean an automatic 230 CFM of airflow will be delivered.

## Slide 5: Zone 1 Pretty Straight Forward
For Zone 1, the air setting task is easy because there is only one position needed for the outside air, bypass, and return dampers (other than closed and off).

## Slide 6: Slight Complication For Zone 2
Maria’s Zone 2’s outside air intake, return and relief ducts will need automated dampers. The three dampers will need be set for two operating positions and linked to synchronize with the kitchen exhaust hood’s two speeds. Finally, for the main trunk, manual dampers are needed to adjust the final airflow to the individual diffusers.

## Slide 7: Zone’s 1 & 2 Balancing Dampers Needed
Finally, for the main trunk, manual dampers are needed to adjust the final airflow to the individual diffusers.

## Slide 8: Double Check the Results
Someone needs to order all of the fittings. A technician needs to make the individual sections of the duct. Installation technicians need to understand how the duct fits into the building. The installation is then followed by the startup where balancing and commissioning technicians need to check air velocities for each supply and return branch, at the maximum and minimum airflow design settings.

## Slide 9: Make Duct Designs User Friendly
Providing information to facilitate balancing and installation with the duct plans is a best practice for designers. A lack of information on how to set the maximum and minimum airflow values in a system like Maria’s restaurant means the startup, balancing, and commissioning people may simply have to guess. Those guesses will often result in a balancing error that can become expensive to resolve. In buildings where that has happened, the design and equipment sizing get questioned. People say “it never has worked, never will work, it all has to be torn out and started over.”

## Slide 10: Manual B Balancing and Testing Air and Hydronic Systems

## Slide 11: Field Changes
Maria Decided She Would Like to be able to shut off the bar area during slow business hours. and her Architect specified some partition doors. (shown in red below).

## Slide 12: Design Question
Identify a problem with Maria’s plan change.
How can the return air get back to the roof top package HVAC system?

## Slide 13: Design Question
Can you offer a solution to Maria and explain why it will save her time and money?

## Slide 14: Design Question
Any time and money saving solution would start with not moving duct or an HVAC system. In this case the designer wanted the return over the heat adding equipment in the bar so that warmer air would not cross over occupied space. Thus, recommend the partition doors be made of an open metal grid style of gate or roll down door rather than a solid material.

## Slide 15: Air Distribution Summary

## Slide 16: Duct Design Question 1
Based on the Air Distribution Design Checklist which of the following should be done if you can only do one?
Make sure there are adequate return air pathways.
Make sure the return is positioned high when the supply duct is positioned low.
Make sure there are adequate return air pathways.

## Slide 17: Duct Design Question 2
Based on the Air Distribution Design Checklist which of the following should be done if you can only do one?
Make sure the blower fan’s airflow is in compliance with the Manufacturer’s data and at the designed value.
Make sure the proper CFM is coming out of every supply diffuser.
Make sure the blower fan’s airflow is in compliance with the Manufacturer’s data and at the designed value.

## Slide 18: Duct Design Question 3
Based on the Air Distribution Design Checklist which of the following should be done if you can only do one?
Do the duct sketch and component list.
Design the component pressure drops.
Do the duct sketch and component list.
Design the component pressure drops.

## Slide 19: Field Notes
Return, Return, Return! Why does seem like everyone ignores the return duct design, and the return path! There are a million horror stories out there. For example, a small store allowed a product display case loaded with high intensity incandescent light bulbs to be placed in the front right side of the store. The heat had to cross the entire store to get back to the return. The call was for AC not working. The AC was working properly, they just chose to heat the air up in the front, and bring it all of the way across the store to the return. The answer was to move the display back to under the return or install a return duct over the display and move some supply diffusers to the back of the store. Not as the store manager wanted a bigger HVAC system. Since the discharge air was the correct temperature, a larger system probably would not have helped.