## Slide 1: 4.0 Equipment Installation Aspects (Section 4.3 Refrigerant Charge)

## Slide 2: Refrigerant Charge
Subcooling
Superheat
OEM Approved Methods
  Weigh In
  Temperature Transfer Charts
  Other Methods?
Acceptable Procedures:

## Slide 3: Refrigerant Charge
NOTE: If outdoor conditions require a follow-up visit to finalize the charging process, this should be recorded at both the initial visit and the follow-up visit.

## Slide 4: Before Hooking Up Gauges
Turn thermostat on and set at full cooling …. lower the set point so it won’t go off while measuring the charge (Steady State Conditions)

## Slide 5: Before Hooking Up Gauges
Let the system settle out…run for 10-15 minutes.
Get documentation together/organized
  Enter equipment data
  Locate OEM charging charts
Get tools together/organized

## Slide 6: Before Hooking Up Gauges
Organizing Tools
Check/calibrate temperature measurement tools
Check gauge set/calibrate
Make sure you have a tool that is designed for removing refrigerant caps
Make sure you have tape cut to size if required for attaching temperature probes to lines
Have a sanding block or sand paper
SP or airflow measurement tools out and ready
Pencil/Pen and paper

## Slide 7: Before Hooking Up Gauges
Verify that the airflow is correct

## Slide 8: Before Hooking Up Gauges
Complete airflow and temperature measurements and then last but not least: hook up gauges

## Slide 9: Before Hooking Up Gauges
Calibration
Screw

## Slide 10: Checking Refrigerant Charge by Subcooling
TXV Valve Bulb

## Slide 11: Clean Surface

## Slide 12: 16 Subcooling

## Slide 13: OEM Subcooling Chart
87 – 81.4 = 5.6

## Slide 14: OEM Subcooling Chart

## Slide 15: Programmable Gauge Set

## Slide 16: Generic Subcooling Chart or App

## Slide 17: What If the charge was wrong?
Add a few ounces of refrigerant …
wait a few minutes and test again
Remove a few ounces of refrigerant …
wait a few minutes and test again
Subcooling higher than target value by 3oF
Subcooling less than target value by 3oF

## Slide 18: Superheat
Cap-Tube

## Slide 19: Superheat
Piston Metering Device

## Slide 20: Superheat
Fixed Orifice Metering Device

## Slide 21: Wet Bulb Temperature

## Slide 22: Condenser Temperature

## Slide 23: Sand and Attach Temperature Probe

## Slide 24: OEM Product Chart

## Slide 25: Generic Charts or Apps

## Slide 26: What If the charge was wrong?
Remove a few ounces of refrigerant …
wait a few minutes and test again
Add a few ounces of refrigerant …
wait a few minutes and test again
Superheat is higher than target value by 5oF
Superheat is less than target value by 5oF

## Slide 27: Other OEM Methods
OEM METHOD MUST BE DOCUMENTED AND EXPLAINED
DATA/PROOF THAT THE OEM PROCEDURE WAS FOLLOWED MUST BE PROVIDED
Exception: weighing in the charge

## Slide 28: Weigh In Charge

## Slide 29
System Needs To Be Empty and pulled down to
at least a 600 micron vacuum
Weigh In Charge

## Slide 30: OEM Charge Listed By Weight

## Slide 31: Line Set Length Adjustment
Additional R-410A Added for Line Length (Weigh In Charge) |  |  | 
Suction Line Size | Ounces per-foot | Liquid Line Size | Ounces per-foot
1/2 | 0.04 | 1/4 | 0.19
5/8 | 0.06 | 5/16 | 0.33
3/4 | 0.09 | 3/8 | 0.51
7/8 | 0.12 | 1/2 | 1.01
1-1/8 | 0.20 | 5/8 | 1.64
Note: generic amounts listed above: use OEM values when available |  |  | 

## Slide 32: Sample Problem
A manufacturer’s allowable length for the refrigerant lines on a heat pump installation is listed as 25 ft. The line sizes are 3/8” for the Liquid side and 7/8” for the suction side. Based on the previously presented generic chart: How much refrigerant is to be added?

## Slide 33: Sample Problem
Additional R-410A Added for Line Length (Weigh In Charge) |  |  | 
Suction Line Size | Ounces per-foot | Liquid Line Size | Ounces per-foot
1/2 | 0.04 | 1/4 | 0.19
5/8 | 0.06 | 5/16 | 0.33
3/4 | 0.09 | 3/8 | 0.51
7/8 | 0.12 | 1/2 | 1.01
1-1/8 | 0.20 | 5/8 | 1.64
Note: generic amounts listed above: use OEM values when available |  |  | 

## Slide 34: Sample Problem
Additional R-410A Added for Line Length (Weigh In Charge) |  |  | 
Suction Line Size | Ounces per-foot | Liquid Line Size | Ounces per-foot
1/2 | 0.04 | 1/4 | 0.19
5/8 | 0.06 | 5/16 | 0.33
3/4 | 0.09 | 3/8 | 0.51
7/8 | 0.12 | 1/2 | 1.01
1-1/8 | 0.20 | 5/8 | 1.64
Note: generic amounts listed above: use OEM values when available |  |  | 

## Slide 35: Sample Problem
Additional R-410A Added for Line Length (Weigh In Charge) |  |  | 
Suction Line Size | Ounces per-foot | Liquid Line Size | Ounces per-foot
1/2 | 0.04 | 1/4 | 0.19
5/8 | 0.06 | 5/16 | 0.33
3/4 | 0.09 | 3/8 | 0.51
7/8 | 0.12 | 1/2 | 1.01
1-1/8 | 0.20 | 5/8 | 1.64
Note: generic amounts listed above: use OEM values when available |  |  | 

## Slide 36: Sample Problem
Additional R-410A Added for Line Length (Weigh In Charge) |  |  | 
Suction Line Size | Ounces per-foot | Liquid Line Size | Ounces per-foot
1/2 | 0.04 | 1/4 | 0.19
5/8 | 0.06 | 5/16 | 0.33
3/4 | 0.09 | 3/8 | 0.51
7/8 | 0.12 | 1/2 | 1.01
1-1/8 | 0.20 | 5/8 | 1.64
Note: generic amounts listed above: use OEM values when available |  |  | 

## Slide 37: Sample Problem
A manufacturer’s allowable length for the refrigerant lines on a heat pump installation is listed as 25 ft. The line sizes are 3/8” for the Liquid side and 3/4” for the suction side. Based on the previously presented generic chart if the line set is 50 ft. long: How much refrigerant is to be added? From the TABLE:
Suction line 0.12 oz. per ft.
Liquid Line 0.51 oz. per ft.

## Slide 38: Sample Problem
A manufacturer’s allowable length for the refrigerant lines on a heat pump installation is listed as 25 ft. The line sizes are 3/8” for the Liquid side and 7/8” for the suction side. Based on the previously presented generic chart if the line set is 50 ft. long: How much refrigerant is to be added? From the TABLE:
Suction line 0.12 oz. per ft.
Liquid Line 0.51 oz. per ft.
Thus, the total additional refrigerant needed is found:
(0.12 X 25) + (0.51 X 25) = 15.75 oz.
Note: the liquid side requires 12.75 oz. for the 3/8” line

## Slide 39: Sample Problem
A manufacturer’s allowable length for the refrigerant lines on a heat pump installation is listed as 25 ft. The line sizes are 3/8” for the Liquid side and 7/8” for the suction side. Based on the previously presented generic chart if the line set is 50 ft. long: How much refrigerant is to be added? From the TABLE:
Suction line 0.12 oz. per ft.
Liquid Line 0.51 oz. per ft.
Thus, the total additional refrigerant needed is found:
(0.12 X 25) + (0.51 X 25) = 15.75 oz.