## Slide 1: 4.0 Equipment Installation Aspects (Section 4.1 Airflow Across the Indoor Heat Exchanger)

## Slide 2: Airflow Across The Indoor Heat Exchanger
Heat Exchangers
The contractor shall ensure measured airflow through the indoor heat exchanger (with all accessories and system components in place).

## Slide 3: Airflow Across The Indoor Heat Exchanger
Airflow in = Airflow out = Airflow across the Heat Exchanger

## Slide 4: Acceptable Procedures (Covered In This Section)
OEM CFM/ESP table method using an air pressure differential meter (e.g. manometer) and probe to determine the static pressure drop across a cooling coil, furnace, or fan coil unit, and compare with OEM provided values (use wet or dry coil information where applicable),
Traversing Method, using a manometer and probe or an anemometer,
Flow Grid measurement Method,

## Slide 5: Acceptable Procedures (Covered In This Section)
Pressure Matching Method (calibrated Fan),
Use of a calibrated fan to match the supply plenum pressure and measurement of the system airflow through the active fan. Note: Methods for use with brushless DC or ECM blowers in accordance with the motor or OEM instructions.
Temperature Rise Method (for heating only: gas or oil furnace, electric resistance heat, geothermal and water source heat pump).

## Slide 6: Acceptable Procedures
Pressure Matching Method (calibrated Fan),
Temperature Rise Method (for heating only: gas or oil furnace, electric resistance heat, geothermal and water source heat pump).
Use of a calibrated fan to match the supply plenum pressure and measurement of the system airflow through the active fan. Note: Methods for use with brushless DC or ECM blowers in accordance with the motor or OEM instructions.

## Slide 7: OEM CFM/ESP Table Method
____
0.60 ESP
Return = - 0.40
(+) 0.20
+ (-) 0.40
Supply = + 0.20
Medium Speed Fan Tap

## Slide 8: Any Calibrated Accurate Pressure Differential Tool Can Measure SP
Magnehelic Gauge
Electronic Manometers

## Slide 9: Warning: Hoses must be securely attached and must not be kinked or pinched
X
X

## Slide 10: External Static Pressure (ESP)
ESP refers to the total difference between two SP measurements that can be used to determine the amount of airflow through an operating HVAC system.
Warning: Read the fine print when dealing with the term External Static Pressure or ESP on engineered built up commercial designs: if the design involves pressurizing the building the ESP may be to the outside of the building.

## Slide 11: External Static Pressure (ESP)
For residential applications, the original equipment manufacturer (OEM) airflow data tables represent the total difference between two SP measurements taken outside of the box provided (in one piece) by the OEM.
Note: If the box includes the coil the
ESP includes the coil

## Slide 12: Measuring External Static Pressure
Based on the OEM box ESP will be the difference between two of the following SP readings:
  In the return duct
  Before the filter
  After the filter
  Before the Blower
  After the blower
  Before the furnace heat exchanger
  After the furnace heat exchanger
  Before the coil
  After the coil
  In the supply duct

## Slide 13: WARNING
Airflow values in CFM on most ESP fan performance charts is based on a known fan speed.

## Slide 14: Finding Fan Speed Based On Wiring

## Slide 15: FAN SPEED BASED ON PIN POSITION

## Slide 16: Fan Performance Chart

## Slide 17: Fan Performance Chart

## Slide 18: Fan Performance Chart

## Slide 19: Traversing
Traversing using a manometer and probe or an anemometer per ACCA, AABC, ASHRAE, ASTM, NEBB, SMACNA, or TABB procedures,

## Slide 20: Laminar Airflow
Even Airflow = Even Pressure
Required for Traversing

## Slide 21: Stratification
Hot and Cold divided
OK for Traversing…Not so good for comfort

## Slide 22: Using SP For Duct Blockage
Turbulence
No Traversing can be done

## Slide 23: Traversing Duct
Airflow
Plane inside of the duct

## Slide 24: Probe Placement For Traversing
Airflow
Points on a plane
VP using a Pitot
tube and a pressure differential gauge

## Slide 25: Probe Placement
2.5 Duct Diameters

## Slide 26: Probe Placement For Traversing
VS

## Slide 27: Equal Spacing Hole Placement
π multiplied by the diameter of the circle = circumference of a circle.
An 8” duct has a diameter of 8” its circumference is: 8 x 3.14 = 25.12 and the distance between the two holes for the traverse = 25.12” ÷ 4 = 6.28”

## Slide 28: Log-T Hole Placement
π multiplied by the diameter of the circle = circumference of a circle. An 8” duct has a diameter of 8” its circumference is: 8 x 3.14 = 25.12 and the distance between the three holes needed for the log-T method = 25.12 ÷ 6 = 4.1867”

## Slide 29: Traverse Readings/Measurements
 | a | b | c | d
1 | 340 | 373 | 320 | 394
2 | 366 | 333 | 352 | 391
3 | 362 | 336 | 365 | 331
Airflow measured in feet per minute (fpm) for 8” round duct.
Average value = Total ÷ 12
4263 ÷ 12 = 355 fpm

## Slide 30: Traverse Readings/Measurements
Airflow in cubic feet per minute (CFM) = Area (A) in square feet (ft2) x fpm.
8” round duct area = π r2
Since the diameter is 8”
radius = 8 ÷ 2 = 4;
π = 3.14 Thus:
A = (3.14 x 42) ÷ 144 = .349 ft2

## Slide 31: Traverse Readings/Measurements
Average airflow = 355 fpm
Area of Duct = .349 ft2
CFM provided by the 8” round duct = .349 x 355 = 124 CFM

## Slide 32: Traverse Readings/Measurements
Average airflow = 355 fpm
Area of Duct = .349 ft2
CFM provided by the 8” round duct = .349 x 355 = 124 CFM

## Slide 33: Traverse Readings/Measurements
Average airflow = 355 fpm
Area of Duct = .349 ft2
CFM provided by the 8” round duct = .349 x 355 = 124 CFM

## Slide 34: Airflow Correction Factors
124 x .81 = 100 CFM of standard air
Air Temp (ºF) | AIR DENSITY / TEMPERATURE CORRECTION FACTORS Altitude In Feet |  |  |  |  |  |  |  |  |  | 
 | 0 | 1000 | 2000 | 3000 | 4000 | 5000 | 6000 | 7000 | 8000 | 9000 | 10000
- 40 | 1.26 | 1.22 | 1.17 | 1.13 | 1.09 | 1.05 | 1.01 | .97 | .93 | .90 | .87
-20 | 1.21 | 1.17 | 1.13 | 1.08 | 1.14 | 1.00 | .97 | .94 | .89 | .86 | .83
0 | 1.15 | 1.11 | 1.07 | 1.03 | .99 | .95 | .92 | .90 | .85 | .82 | .80
20 | 1.10 | 1.06 | 1.03 | 1.00 | .96 | .92 | .89 | .86 | .82 | .79 | .76
40 | 1.06 | 1.02 | .99 | .96 | .92 | .88 | .86 | .82 | .79 | .76 | .74
50 | 1.04 | 1.00 | .97 | .94 | .90 | .87 | .84 | .81 | .78 | .75 | .73
55 | 1.03 | .99 | .96 | .93 | .89 | .86 | .83 | .80 | .77 | .74 | .72
60 | 1.02 | .98 | .95 | .91 | .88 | .85 | .82 | .79 | .76 | .73 | .71
70 | 1.00* | .96 | .93 | .89 | .86 | .83 | .80 | .77 | .75 | .71 | .69
80 | .99 | .95 | .92 | .88 | .85 | .81 | .79 | .76 | .74 | .70 | .68
90 | .97 | .94 | .90 | .86 | .83 | .80 | .77 | .75 | .72 | .69 | .67
100 | .95 | .93 | .88 | .85 | .81 | .78 | .75 | .73 | .70 | .68 | .66
110 | .94 | .92 | .86 | .83 | .80 | .77 | .74 | .72 | .69 | .67 | .65
120 | .93 | .90 | .85 | .82 | .79 | .76 | .73 | .71 | .68 | .66 | .64
130 | .91 | .88 | .83 | .81 | .78 | .75 | .72 | .70 | .67 | .64 | .63
140 | .89 | .86 | .81 | .80 | .77 | .73 | .71 | .68 | .66 | .63 | .61
150 | .87 | .84 | .80 | .79 | .75 | .72 | .70 | .67 | .65 | .62 | .60
160 | .86 | .83 | .79 | .78 | .74 | .71 | .69 | .66 | .64 | .61 | .59
170 | .85 | .82 | .77 | .76 | .73 | .70 | .68 | .65 | .63 | .60 | .58
180 | .83 | .80 | .76 | .75 | .71 | .68 | .67 | .64 | .62 | .59 | .57
190 | .81 | .79 | .75 | .73 | .69 | .67 | .66 | .63 | .61 | .58 | .56
200 | .80 | .77 | .74 | .71 | .68 | .66 | .64 | .62 | .60 | .57 | .55
250 | .75 | .72 | .70 | .67 | .64 | .62 | .60 | .58 | .56 | .54 | .51
500 | .55 | .53 | .51 | .49 | .47 | .45 | .44 | .43 | .41 | .39 | .38
1000 | .36 | .35 | .33 | .32 | .31 | .30 | .29 | .28 | .27 | .26 | .25
Standard Air density for HVAC is 70ºF, 0.075 Lbm/Ft3, at sea level (or 0 ft), and 29.92 in Hg. |  |  |  |  |  |  |  |  |  |  | 
.81

## Slide 35: Other Traversing Tools

## Slide 36: FLOW GRID METHOD
1. Static Pressure is measured in the supply Duct.

## Slide 37: FLOW GRID METHOD
2. Flow Grid is fitted and installed so no airflow can bypass the Flow Grid (must go through it)

## Slide 38: FLOW GRID METHOD
3. Pressure drop across the Flow Grid is measured
and

## Slide 39: FLOW GRID METHOD
4. Static Pressure is measured in the supply Duct
and if required Flow Grid Manufacturer’s correction
factors are applied to calculate the airflow.

## Slide 40: Pressure Matching Method
Uses a Calibrated Fan with
a fixed orifice to establish
CFM.

## Slide 41: Daniel Bernoulli’ Principle
airflow
airflow
Pressure at Inlet
Pressure at Outlet
Fixed Orifice (hole)
The pressure drop across a fixed
orifice can be equated to CFM

## Slide 42: Pressure Matching Method
Uses a Calibrated Fan with
a fixed orifice to establish
CFM.
Manufactures Instructions
for the tool need to be
followed

## Slide 43: Pressure Matching Method
This procedure is often done in
Conjunction with duct leakage
Testing using the same tool and
Setup.

## Slide 44: Pressure Matching Method
For larger HVAC systems that exceed the airflow that can be produced by the calibrated fan, most tool manufacturers will have correction factors.
The correction factors will be based on the static pressure measured at the supply duct before the test equipment was set up and a value at the top test fan speed.

## Slide 45: Pressure Matching Method
For larger HVAC systems that exceed the airflow that can be produced by the calibrated fan, most tool manufacturers will have correction factors.
The correction factors will be based on the static pressure measured at the supply duct before the test equipment was set up and a value at the top test fan speed.

## Slide 46: Temperature Rise Method
For Evaluating Heating Systems Only
Air temperature on both sides of the heat exchanger is measured.

## Slide 47: Temperature Rise Method
Return Temperature
Supply Temperature

## Slide 48: Temperature Rise Method
Supply Temperature – Return Temperature
is compared to a Manufacturer’s table
Two rules will always apply:
The probes have to measure the average
temperature accurately for the table to work.
The unit must be operating properly
(combustion process or electrical power)