## KW (hidden)
L | 10 | 20
M | 20
H | 30
Room
Zone
Block
Altitude | ACF |  | 0 | 20 | 25
0 | 1 |  | 22 | 25
500 | 0.99 |  | 27 | 30
750 | 0.98 |  | 32 | 35
1000 | 0.97 |  | 37 | 40
1250 | 0.96 |  | 42 | 45
1500 | 0.95 |  | 47 | 50
1750 | 0.94 |  | 52 | 55
2000 | 0.93 |  | 57 | 60
2250 | 0.92 |  | 62 | 65
2500 | 0.91 |  | 67 | 70
2750 | 0.9 |  | 72 | 75
3000 | 0.89 |  | 77 | 80
3500 | 0.88 |  | 82 | 85
4000 | 0.87 |  | 87 | 90
4333 | 0.86 |  | 92 | 95
4666 | 0.85
5000 | 0.84
5250 | 0.83
5500 | 0.82
5750 | 0.81
6000 | 0.8
6333 | 0.79
6666 | 0.78
7000 | 0.77
7500 | 0.76
8000 | 0.75
8333 | 0.74
8666 | 0.73
9000 | 0.72
9333 | 0.71
9666 | 0.7
10000 | 0.69
10333 | 0.68
10666 | 0.67
11000 | 0.66
11333 | 0.65
11666 | 0.64
12000 | 0.63
9:00 | 0.71 | 0 | 2 | 9 | 1
12:00 | 0.23 |  | 3 | 12 | 2
15:00 | 0 |  | 4 | 15 | 3 |  |  |  | Example Index & Match = Lookup
18:00 | 0.21 |  | 5 | 18 | 4 |  |  |  |  | a | b | c | d
[9 empty] | 1 | 1a | 1b | 1c | 1d
45 | [8 empty] | 2 | 2a | 2b | 2c | 2d
50 | [8 empty] | 3 | 3a | 3b | 3c | 3d
55
3
Metal No Break | [9 empty] | d
Metal with Break | [9 empty] | 3d
Wood or wood clad
Insulated Fiberglass
| Latitude | [6 empty] | Lower | Interpolated | Higher
| 20 | 28 | 36 | 44 | 52 | 60 |  | 28 | 34 | 36
East | 220 | 220 | 218 | 214 | 208 | 199 |  | 220 | 218.5 | 218
Horizontal | 280 | 272 | 257 | 236 | 208 | 176 |  | 272 | 260.75 | 257
NE | 162 | 149 | 138 | 132 | 124 | 114 |  | 149 | 140.75 | 138
North | 40 | 38 | 36 | 34 | 32 | 28 |  | 38 | 36.5 | 36
NW | 162 | 149 | 138 | 132 | 124 | 114 |  | 149 | 140.75 | 138
SE | 152 | 172 | 189 | 202 | 212 | 217 |  | 172 | 184.75 | 189
South | 57 | 91 | 131 | 165 | 193 | 211 |  | 91 | 121 | 131
SW | 152 | 172 | 189 | 202 | 212 | 217 |  | 172 | 184.75 | 189
West | 220 | 220 | 218 | 214 | 208 | 199 |  | 220 | 218.5 | 218
Latitude
20 | 28 |  |  |  | Light | 6 | 7 | 8 | 9
28 | 36 |  |  |  | Medium | 10 | 11 | 12 | 13
36 | 44 |  |  |  | Heavy | 14 | 15 | 16 | 17
44 | 52 |  |  |  | Internal Shade | 18 | 19 | 20 | 21
52 | 60
60 | 68
| 10 | 11 | 12 | 13 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21
Time | 9 | 12 | 3 | 6 | 9 | 12 | 3 | 6 | 9 | 12 | 3 | 6 | 9 | 12 | 3 | 6 | 9 | 12 | 3 | 6
North | 0.53 | 0.7 | 0.76 | 0.79 | 0.56 | 0.76 | 0.82 | 0.84 | 0.53 | 0.7 | 0.76 | 0.79 | 0.55 | 0.69 | 0.72 | 0.75 | 0.73 | 0.89 | 0.82 | 0.91
NE | 0.45 | 0.33 | 0.28 | 0.21 | 0.51 | 0.36 | 0.28 | 0.19 | 0.45 | 0.33 | 0.28 | 0.21 | 0.44 | 0.31 | 0.26 | 0.2 | 0.58 | 0.27 | 0.22 | 0.12
East | 0.5 | 0.39 | 0.29 | 0.21 | 0.57 | 0.42 | 0.29 | 0.19 | 0.5 | 0.39 | 0.29 | 0.21 | 0.49 | 0.36 | 0.26 | 0.19 | 0.76 | 0.27 | 0.2 | 0.11
SE | 0.48 | 0.551 | 0.36 | 0.25 | 0.55 | 0.57 | 0.37 | 0.24 | 0.48 | 0.551 | 0.36 | 0.25 | 0.49 | 0.48 | 0.33 | 0.24 | 0.81 | 0.49 | 0.25 | 0.13
South | 0.21 | 0.52 | 0.53 | 0.36 | 0.22 | 0.59 | 0.59 | 0.36 | 0.21 | 0.52 | 0.53 | 0.36 | 0.24 | 0.51 | 0.5 | 0.32 | 0.38 | 0.83 | 0.5 | 0.19
SW | 0.13 | 0.23 | 0.53 | 0.53 | 0.12 | 0.24 | 0.6 | 0.58 | 0.13 | 0.23 | 0.53 | 0.53 | 0.16 | 0.25 | 0.52 | 0.49 | 0.16 | 0.38 | 0.83 | 0.45
West | 0.11 | 0.14 | 0.4 | 0.55 | 0.1 | 0.14 | 0.45 | 0.61 | 0.11 | 0.14 | 0.4 | 0.55 | 0.14 | 0.16 | 0.4 | 0.52 | 0.13 | 0.17 | 0.72 | 0.61
NW | 0.13 | 0.17 | 0.3 | 0.54 | 0.12 | 0.17 | 0.33 | 0.6 | 0.13 | 0.17 | 0.3 | 0.54 | 0.15 | 0.18 | 0.3 | 0.51 | 0.17 | 0.21 | 0.52 | 0.69
Horizontal | 0.33 | 0.59 | 0.66 | 0.47 | 0.36 | 0.66 | 0.73 | 0.47 | 0.33 | 0.59 | 0.66 | 0.47 | 0.36 | 0.59 | 0.62 | 0.42 | 0.59 | 0.85 | 0.71 | 0.25
Shade Line Multipliers | [6 empty] | 20 | 20 | 20 | 20 | 28 | 28 | 28 | 28 | 36 | 36 | 36 | 36 | 44 | 44 | 44 | 44 | 52 | 52 | 52 | 52 | 60 | 60 | 60 | 60
[7 empty] | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
| 28 |  | 34 | 36 |  |  | 201 | 202 | 203 | 204 | 281 | 282 | 283 | 284 | 361 | 362 | 363 | 364 | 441 | 442 | 443 | 444 | 521 | 522 | 523 | 524 | 601 | 602 | 603 | 604
East | 283 | 0 | 0 | 363 | 0 | East | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0
NE | 283 | 0 | 0 | 363 | 0 | NE | 1.6 | 0 | 0 | 0 | 2.8 | 0 | 0 | 0 | 2.2 | 0 | 0 | 0 | 2.5 | 0 | 0 | 0 | 3.1 | 0 | 0 | 0 | 3.9 | 0 | 0 | 0
North | 283 | 0 | 0 | 363 | 0 | North | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NW | 283 | 1.8 | 2.1 | 363 | 2.2 | NW | 0 | 0 | 1.6 | 0.1 | 0 | 0 | 1.8 | 0.1 | 0 | 0 | 2.2 | 0 | 0 | 0 | 2.5 | 0.2 | 0 | 0 | 3.1 | 0.2 | 0 | 0 | 3.9 | 0.2
SE | 283 | 0 | 0 | 363 | 0 | SE | 1.4 | 12.7 | 0 | 0 | 1.2 | 5 | 0 | 0 | 1 | 3.1 | 0 | 0 | 0.8 | 2.2 | 0 | 0 | 0.7 | 1.6 | 0 | 0 | 0.6 | 1.2 | 0 | 0
South | 283 | 5.3 | 3.425 | 363 | 2.8 | South | 3.5 | 9.5 | 3.5 | 0 | 5.3 | 3.7 | 5.3 | 0 | 2.8 | 2.3 | 2.8 | 0.2 | 1.9 | 1.6 | 1.9 | 0 | 1.4 | 1.2 | 1.4 | 0 | 1 | 0.9 | 1 | 0
SW | 283 | 1.2 | 1.05 | 363 | 1 | SW | 0 | 12.7 | 1.4 | 0.1 | 0 | 5 | 1.2 | 0.1 | 0 | 3.1 | 1 | 0.1 | 0 | 2.5 | 0.8 | 0.2 | 0 | 1.6 | 0.7 | 0.2 | 0 | 1.2 | 0.6 | 0.3
West | 283 | 1 | 1 | 363 | 1 | West | 0 | 0 | 1 | 0.1 | 0 | 0 | 1 | 0.1 | 0 | 0 | 1 | 0.1 | 0 | 0 | 0.9 | 0.1 | 0 | 0 | 0.8 | 0.2 | 0 | 0 | 0.7 | 0.2
CLF Values | [6 empty] | 1 281: None; 2 282: 1
15:00 | 4 |  | None |  | 1 |  | 1 201: None; 3 203: 0.23; 1 281: Blinds @ 45°; 2 282: 0.8
North | 0.76 |  | Insect Screen |  | 0.9 |  | 1 201: 10°,Dark,23 S/I; 3 203: 0.33
NE | 0.28 |  | Bay Window |  | 1.15 |  | 1 201: 10°,Light,23 S/I; 3 203: 0.51
East | 0.29 |  | Garden Window |  | 2 |  | 1 201: 10°,Dark,17 S/I; 3 203: 0.59
SE | 0.36 | [5 empty] | 1 201: 10°,Dark,17 S/I; 3 203: 0.06
South | 0.53 | [5 empty] | 1 201: 20°,Dark,23 S/I; 3 203: 0.23
SW | 0.53 | [5 empty] | 1 201: 20°,Light,23 S/I; 3 203: 0.42
West | 0.4 | [5 empty] | 1 201: 20°,Dark,17 S/I; 3 203: 0.5
NW | 0.3 | [5 empty] | 1 201: 20°,Dark,17 S/I; 3 203: 0.04
Horizontal | 0.66 | [5 empty] | 1 201: 30°,Dark,23 S/I; 3 203: 0.21
[7 empty] | 30°,Light,23 S/I |  | 0.31
CLTD values for doors | [6 empty] | 1 201: 30°,Dark,17 S/I; 3 203: 0.38
13 | M | 15 | 15M |  |  |  | 1 201: 30°,Dark,17 S/I; 3 203: 0.04
Calculated CLTD |  | 26 |  |  |  |  | 1 201: 40°,Dark,23 S/I; 3 203: 0.2
|  | Design | CLTD | Const 20 |  |  | 1 201: 40°,Light,23 S/I; 3 203: 0.18
-10 | 10 | 10L | 25 | 9 |  |  | 1 201: 40°,Dark,17 S/I; 3 203: 0.3
11 | 10 | 10M | 21 | 5 |  |  | 1 201: 40°,Dark,17 S/I; 3 203: 0.04
12 | 10 | 15L | 30 | 14 |  |  | 1 201: 50°,Dark,23 S/I; 3 203: 0.2
13 | 15 | 15M | 26 | 10 |  |  | 1 201: 50°,Light,23 S/I; 3 203: 0.18
14 | 15 | 15H | 21 | 5 |  |  | 1 201: 50°,Dark,17 S/I; 3 203: 0.3
15 | 15 | 20L | 35 | 19 |  |  | 1 201: 50°,Dark,17 S/I
16 | 15 | 20M | 31 | 15
17 | 15 | 20H | 26 | 10
18 | 20 | 25M | 36 | 20
19 | 20 | 25H | 31 | 15
20 | 20 | 30H | 36 | 20
21 | 20 | 35H | 41 | 25
22 | 20
23 | 25
24 | 25
25 | 25
26 | 25
27 | 25
28 | 30
29 | 30
30 | 30
31 | 30
32 | 30
33 | 35
34 | 35
35 | 35
Wall CLTD Values and Group Numbers
Time | 15
| A9 | A12 | A15 | A18 | B9 | B12 | B15 | B18 | C9 | C12 | C15 | C18 | D9 | D12 | D15 | D18 | E9 | E12 | E15 | E18 | F9 | F12 | F15 | F18 | G9 | G12 | G15 | G18 | H9 | H12 | H15 | H18 | I9 | I12 | I15 | I18 | J9 | J12 | J15 | J18 | K9 | K12 | K15 | K18
East | 48 | 36 | 28 | 23 | 37 | 38 | 30 | 25 | 26 | 40 | 33 | 28 | 22 | 37 | 33 | 29 | 18 | 33 | 33 | 30 | 15 | 29 | 32 | 30 | 13 | 25 | 30 | 30 | 14 | 23 | 29 | 29 | 15 | 21 | 27 | 28 | 15 | 20 | 25 | 26 | 15 | 19 | 23 | 25
NE | 35 | 25 | 25 | 21 | 29 | 26 | 25 | 23 | 22 | 27 | 25 | 25 | 19 | 25 | 25 | 25 | 15 | 24 | 25 | 25 | 13 | 22 | 23 | 24 | 11 | 20 | 22 | 24 | 12 | 18 | 21 | 23 | 12 | 17 | 20 | 22 | 13 | 16 | 19 | 21 | 13 | 15 | 18 | 20
North | 10 | 18 | 23 | 25 | 9 | 15 | 21 | 23 | 8 | 12 | 19 | 22 | 8 | 11 | 17 | 21 | 7 | 10 | 15 | 20 | 8 | 10 | 14 | 18 | 8 | 9 | 13 | 17 | 9 | 9 | 12 | 16 | 10 | 10 | 11 | 15 | 10 | 10 | 11 | 14 | 10 | 10 | 10 | 13
NW | 10 | 18 | 34 | 49 | 8 | 15 | 27 | 43 | 5 | 11 | 20 | 38 | 6 | 10 | 16 | 34 | 7 | 10 | 16 | 30 | 8 | 10 | 15 | 25 | 10 | 10 | 13 | 21 | 11 | 10 | 13 | 20 | 12 | 11 | 13 | 18 | 13 | 12 | 13 | 17 | 15 | 13 | 13 | 15
SE | 38 | 43 | 30 | 23 | 28 | 40 | 32 | 26 | 19 | 37 | 35 | 29 | 16 | 33 | 35 | 30 | 13 | 29 | 34 | 30 | 12 | 25 | 31 | 30 | 11 | 21 | 29 | 30 | 12 | 20 | 27 | 28 | 13 | 19 | 25 | 27 | 14 | 18 | 23 | 25 | 15 | 16 | 20 | 24
South | 13 | 35 | 39 | 24 | 9 | 27 | 32 | 28 | 5 | 20 | 26 | 32 | 6 | 17 | 27 | 31 | 6 | 14 | 27 | 30 | 7 | 12 | 23 | 29 | 8 | 10 | 20 | 27 | 9 | 11 | 18 | 25 | 10 | 11 | 17 | 23 | 12 | 12 | 16 | 21 | 13 | 12 | 15 | 19
SW | 10 | 25 | 52 | 46 | 8 | 18 | 42 | 47 | 6 | 12 | 32 | 47 | 7 | 11 | 27 | 43 | 7 | 10 | 23 | 39 | 9 | 10 | 20 | 34 | 10 | 10 | 16 | 30 | 12 | 11 | 16 | 27 | 14 | 12 | 15 | 25 | 15 | 13 | 15 | 22 | 16 | 15 | 15 | 20
West | 10 | 19 | 49 | 59 | 8 | 15 | 38 | 54 | 6 | 12 | 26 | 50 | 7 | 11 | 23 | 45 | 8 | 10 | 20 | 39 | 10 | 10 | 17 | 33 | 11 | 10 | 15 | 28 | 13 | 12 | 15 | 25 | 15 | 13 | 15 | 23 | 16 | 14 | 15 | 21 | 18 | 15 | 15 | 19
Walls Color Adjustment
Dark | 15 A9: 1.2
Default | bar: 15 A9
White | 15 A9: 0.78
| 16A9 | 16A12 | 16A15 | 16A18 | 16B9 | 16B12 | 16B15 | 16B18 | 16BR9 | 16BR12 | 16BR15 | 16BR18 | 16C9 | 16C12 | 16C15 | 16C18 | 16CR9 | 16CR12 | 16CR15 | 16CR18 | 16D9 | 16D12 | 16D15 | 16D18 | 16DR9 | 16DR12 | 16DR15 | 16DR18 | 16E9 | 16E12 | 16E15 | 16E18 | 16ER9 | 16ER12 | 16ER15 | 16ER18 | 16F9 | 16F12 | 16F15 | 16F18 | 16FR9 | 16FR12 | 16FR15 | 16FR18
10L | 27 | 59 | 69 | 64 | 19 | 42 | 49 | 45 | 19 | 42 | 49 | 45 | 27 | 59 | 69 | 64 | 27 | 59 | 69 | 64 | 11 | 24 | 29 | 26 | 11 | 24 | 29 | 26 | 9 | 20 | 24 | 21 | 9 | 20 | 24 | 21 | 5 | 11 | 14 | 12 | 5 | 11 | 14 | 12
10M | 18 | 53 | 65 | 58 | 10 | 36 | 45 | 39 | 10 | 36 | 45 | 39 | 18 | 53 | 65 | 58 | 18 | 53 | 65 | 58 | 2 | 18 | 25 | 20 | 2 | 18 | 25 | 20 | 0 | 14 | 20 | 15 | 0 | 14 | 20 | 15 | -4 | 5 | 10 | 6 | -4 | 5 | 10 | 6
15L | 32 | 64 | 74 | 69 | 24 | 47 | 54 | 50 | 24 | 47 | 54 | 50 | 32 | 64 | 74 | 69 | 32 | 64 | 74 | 69 | 16 | 29 | 34 | 31 | 16 | 29 | 34 | 31 | 14 | 25 | 29 | 26 | 14 | 25 | 29 | 26 | 10 | 16 | 19 | 17 | 10 | 16 | 19 | 17
15M | 23 | 58 | 70 | 63 | 15 | 41 | 50 | 44 | 15 | 41 | 50 | 44 | 23 | 58 | 70 | 63 | 23 | 58 | 70 | 63 | 7 | 23 | 30 | 25 | 7 | 23 | 30 | 25 | 5 | 19 | 25 | 20 | 5 | 19 | 25 | 20 | 1 | 10 | 15 | 11 | 1 | 10 | 15 | 11
15H | 14 | 52 | 75 | 56 | 6 | 34 | 45 | 37 | 6 | 34 | 45 | 37 | 14 | 52 | 65 | 56 | 14 | 52 | 65 | 56 | -2 | 17 | 25 | 18 | -2 | 17 | 25 | 18 | -4 | 12 | 20 | 13 | -4 | 12 | 20 | 13 | -8 | 4 | 10 | 4 | -8 | 4 | 10 | 4
20L | 37 | 69 | 79 | 74 | 29 | 52 | 59 | 55 | 29 | 52 | 59 | 55 | 37 | 69 | 79 | 74 | 37 | 69 | 79 | 74 | 21 | 34 | 39 | 36 | 21 | 34 | 39 | 36 | 19 | 30 | 34 | 31 | 19 | 30 | 34 | 31 | 15 | 21 | 24 | 22 | 15 | 21 | 24 | 22
20M | 28 | 63 | 75 | 68 | 20 | 46 | 55 | 49 | 20 | 46 | 55 | 49 | 28 | 63 | 75 | 68 | 28 | 63 | 75 | 68 | 12 | 28 | 35 | 30 | 12 | 28 | 35 | 30 | 10 | 24 | 30 | 25 | 10 | 24 | 30 | 25 | 6 | 15 | 20 | 16 | 6 | 15 | 20 | 16
20H | 19 | 57 | 70 | 61 | 11 | 39 | 50 | 42 | 11 | 39 | 50 | 42 | 19 | 57 | 70 | 61 | 19 | 57 | 70 | 61 | 3 | 22 | 30 | 23 | 3 | 22 | 30 | 23 | 1 | 17 | 25 | 18 | 1 | 17 | 25 | 18 | -3 | 9 | 15 | 9 | -3 | 9 | 15 | 9
25M | 23 | 68 | 80 | 73 | 25 | 51 | 60 | 54 | 25 | 51 | 60 | 54 | 33 | 68 | 80 | 73 | 33 | 68 | 80 | 73 | 17 | 33 | 40 | 35 | 17 | 33 | 40 | 35 | 15 | 29 | 35 | 30 | 15 | 29 | 35 | 30 | 11 | 20 | 25 | 21 | 11 | 20 | 25 | 21
25H | 24 | 62 | 75 | 6 | 16 | 44 | 55 | 47 | 16 | 44 | 55 | 47 | 24 | 62 | 75 | 66 | 24 | 62 | 75 | 66 | 8 | 27 | 35 | 28 | 8 | 27 | 35 | 28 | 6 | 22 | 30 | 23 | 6 | 22 | 30 | 23 | 2 | 14 | 20 | 14 | 2 | 14 | 20 | 14
30H | 29 | 67 | 80 | 71 | 21 | 49 | 60 | 52 | 21 | 49 | 60 | 52 | 29 | 67 | 80 | 71 | 29 | 67 | 80 | 71 | 13 | 22 | 40 | 33 | 13 | 22 | 40 | 33 | 11 | 27 | 35 | 28 | 11 | 27 | 35 | 28 | 7 | 19 | 25 | 19 | 7 | 19 | 25 | 19
35H | 34 | 72 | 85 | 76 | 26 | 54 | 65 | 57 | 26 | 54 | 65 | 57 | 34 | 72 | 85 | 76 | 34 | 72 | 85 | 76 | 18 | 37 | 45 | 38 | 18 | 37 | 45 | 38 | 16 | 32 | 40 | 33 | 16 | 32 | 40 | 33 | 12 | 24 | 30 | 24 | 12 | 24 | 30 | 24
4 | 0.78 16A9: 9; 0.78 16A12: 12; 0.78 16A15: 15; 0.78 16A18: 18; 0.78 16B12: 15M
16A | 0.78 16A9: 23; 0.78 16A12: 58; 0.78 16A15: 70; 0.78 16A18: 63; 0.78 16B12: 16A9; 0.78 16B15: 23; 0.78 16B18: 16A12; 0.78 16BR9: 58; 0.78 16BR12: 16A15; 0.78 16BR15: 70; 0.78 16BR18: 16A18; 0.78 16C9: 63
16B | 0.78 16A9: 15; 0.78 16A12: 41; 0.78 16A15: 50; 0.78 16A18: 44; 0.78 16B12: 16B9; 0.78 16B15: 15; 0.78 16B18: 16B12; 0.78 16BR9: 41; 0.78 16BR12: 16B15; 0.78 16BR15: 50; 0.78 16BR18: 16B18; 0.78 16C9: 44
16C | 0.78 16A9: 23; 0.78 16A12: 58; 0.78 16A15: 70; 0.78 16A18: 63; 0.78 16B12: 16C9; 0.78 16B15: 23; 0.78 16B18: 16C12; 0.78 16BR9: 58; 0.78 16BR12: 16C15; 0.78 16BR15: 70; 0.78 16BR18: 16C18; 0.78 16C9: 63
16D | 0.78 16A9: 7; 0.78 16A12: 23; 0.78 16A15: 30; 0.78 16A18: 25; 0.78 16B12: 16D9; 0.78 16B15: 7; 0.78 16B18: 16D12; 0.78 16BR9: 23; 0.78 16BR12: 16D15; 0.78 16BR15: 30; 0.78 16BR18: 16D18; 0.78 16C9: 25
16E | 0.78 16A9: 5; 0.78 16A12: 19; 0.78 16A15: 25; 0.78 16A18: 20; 0.78 16B12: 16E9; 0.78 16B15: 5; 0.78 16B18: 16E12; 0.78 16BR9: 19; 0.78 16BR12: 16E15; 0.78 16BR15: 25; 0.78 16BR18: 16E18; 0.78 16C9: 20
16F | 0.78 16A9: 1; 0.78 16A12: 10; 0.78 16A15: 15; 0.78 16A18: 11; 0.78 16B12: 16F9; 0.78 16B15: 1; 0.78 16B18: 16F12; 0.78 16BR9: 10; 0.78 16BR12: 16F15; 0.78 16BR15: 15; 0.78 16BR18: 16F18; 0.78 16C9: 11
R1 | 0.78 16A9: 31; 0.78 16A12: 62; 0.78 16A15: 67; 0.78 16A18: 40
R2 | 0.78 16A9: 15; 0.78 16A12: 46; 0.78 16A15: 64; 0.78 16A18: 54
R3 | 0.78 16A9: 10; 0.78 16A12: 40; 0.78 16A15: 61; 0.78 16A18: 58
R4 | 0.78 16A9: 12; 0.78 16A12: 37; 0.78 16A15: 57; 0.78 16A18: 54
R5 | 0.78 16A9: 7; 0.78 16A12: 35; 0.78 16A15: 55; 0.78 16A18: 50
R6 | 0.78 16A9: 8; 0.78 16A12: 27; 0.78 16A15: 47; 0.78 16A18: 49
R7 | 0.78 16A9: 5; 0.78 16A12: 22; 0.78 16A15: 45; 0.78 16A18: 56
R8 | 0.78 16A9: 8; 0.78 16A12: 20; 0.78 16A15: 38; 0.78 16A18: 49
R9 | 0.78 16A9: 9; 0.78 16A12: 18; 0.78 16A15: 35; 0.78 16A18: 46
R10 | 0.78 16A9: 9; 0.78 16A12: 14; 0.78 16A15: 30; 0.78 16A18: 45
R12 | 0.78 16A9: 11; 0.78 16A12: 25; 0.78 16A15: 41; 0.78 16A18: 47
R13 | 0.78 16A9: 10; 0.78 16A12: 17; 0.78 16A15: 33; 0.78 16A18: 44
R14 | 0.78 16A9: 15; 0.78 16A12: 21; 0.78 16A15: 33; 0.78 16A18: 40
R15 | 0.78 16A9: 18; 0.78 16A12: 17; 0.78 16A15: 25; 0.78 16A18: 33
RC1 | 0.78 16A9: 22; 0.78 16A12: 54; 0.78 16A15: 68; 0.78 16A18: 49
RC2 | 0.78 16A9: 9; 0.78 16A12: 28; 0.78 16A15: 49; 0.78 16A18: 54
RC3 | 0.78 16A9: 16; 0.78 16A12: 27; 0.78 16A15: 49; 0.78 16A18: 56
RC4 | 0.78 16A9: 15; 0.78 16A12: 24; 0.78 16A15: 35; 0.78 16A18: 42
RC5 | 0.78 16A9: 9; 0.78 16A12: 24; 0.78 16A15: 43; 0.78 16A18: 50
RC6 | 0.78 16A9: 12; 0.78 16A12: 21; 0.78 16A15: 35; 0.78 16A18: 44
RC7 | 0.78 16A9: 9; 0.78 16A12: 16; 0.78 16A15: 33; 0.78 16A18: 46
RC8 | 0.78 16A9: 15; 0.78 16A12: 18; 0.78 16A15: 28; 0.78 16A18: 37
RC9 | 0.78 16A9: 17; 0.78 16A12: 19; 0.78 16A15: 27; 0.78 16A18: 36
RC10 | 0.78 16A9: 15; 0.78 16A12: 15; 0.78 16A15: 24; 0.78 16A18: 35
RC12 | 0.78 16A9: 20; 0.78 16A12: 23; 0.78 16A15: 20; 0.78 16A18: 35
RC13 | 0.78 16A9: 18; 0.78 16A12: 20; 0.78 16A15: 36; 0.78 16A18: 35
RC14 | 0.78 16A9: 20; 0.78 16A12: 22; 0.78 16A15: 26; 0.78 16A18: 30
RC15 | 0.78 16A9: 23; 0.78 16A12: 20; 0.78 16A15: 23; 0.78 16A18: 28
RJ2 | 0.78 16A9: 9; 0.78 16A12: 28; 0.78 16A15: 49; 0.78 16A18: 54
RJ5 | 0.78 16A9: 9; 0.78 16A12: 24; 0.78 16A15: 43; 0.78 16A18: 50
RJ6 | 0.78 16A9: 12; 0.78 16A12: 21; 0.78 16A15: 35; 0.78 16A18: 44
RJ8 | 0.78 16A9: 15; 0.78 16A12: 18; 0.78 16A15: 28; 0.78 16A18: 37
RJ13 | 0.78 16A9: 18; 0.78 16A12: 20; 0.78 16A15: 26; 0.78 16A18: 35
RJ15 | 0.78 16A9: 23; 0.78 16A12: 20; 0.78 16A15: 23; 0.78 16A18: 28
Floors 20B
CF2 | 0.78 16A9: 2; 0.78 16A12: 7; 0.78 16A15: 15; 0.78 16A18: 20
CF3 | 0.78 16A9: 0; 0.78 16A12: 6; 0.78 16A15: 15; 0.78 16A18: 20
CF5 | 0.78 16A9: 2; 0.78 16A12: 4; 0.78 16A15: 12; 0.78 16A18: 18
CF7 | 0.78 16A9: 2; 0.78 16A12: 0; 0.78 16A15: 7; 0.78 16A18: 16
CF10 | 0.78 16A9: 5; 0.78 16A12: 0; 0.78 16A15: 2; 0.78 16A18: 10
CF13 | 0.78 16A9: 6; 0.78 16A12: 2; 0.78 16A15: 3; 0.78 16A18: 10
CF15 | 0.78 16A9: 9; 0.78 16A12: 3; 0.78 16A15: 2; 0.78 16A18: 6
[6 empty] | Sq. Ft. | Column | 1117
1 or 2 Exposures | 0.78 16A9: 5D; 0.78 16A12: 5D; 0.78 16A15: Single Story; 0.78 16A18: 1; 0.78 16B9: 1; 0.78 16B12: 0; 0.78 16B15: 1; 0.78 16B18: 2; 0.78 16BR9: Tight
3 or 4 Exposures | 0.78 16A9: 5C; 0.78 16A15: Multi Level; 0.78 16A18: 2; 0.78 16B12: 1001; 0.78 16B15: 2; 0.78 16BR9: Semi-Tight
[6 empty] | 5001 | 3 |  | Average
[6 empty] | 10001 | 4 |  | Semi-Loose
|  | Htg | Clg |  |  | 15000 | 5 |  | Loose
Average | 0.78 16A9: 5D12; 0.78 16A12: 0.62; 0.78 16A15: 0.33
| 5C11 | 5C12 | 5C13 | 5C14 | 5C15 | 5C21 | 5C22 | 5C23 | 5C24 | 5C25 | 5D11 | 5D12 | 5D13 | 5D14 | 5D15 | 5D21 | 5D22 | 5D23 | 5D24 | 5D25
Average | 1.31 | 0.81 | 0.59 | 0.49 | 0.42 | 2.05 | 1.04 | 0.65 | 0.52 | 0.3 | 0.91 | 0.62 | 0.49 | 0.42 | 0.36 | 1.18 | 0.65 | 0.44 | 0.35 | 0.29
Loose | 2.25 | 1.38 | 1 | 0.84 | 0.71 | 3.52 | 1.79 | 1.12 | 0.89 | 0.52 | 1.57 | 1.07 | 0.83 | 0.72 | 0.61 | 2.02 | 1.12 | 0.75 | 0.6 | 0.49
Semi-Loose | 1.76 | 1.1 | 0.79 | 0.66 | 0.56 | 2.79 | 1.42 | 0.89 | 0.7 | 0.41 | 1.24 | 0.85 | 0.66 | 0.57 | 0.49 | 1.6 | 0.89 | 0.59 | 0.48 | 0.39
Semi-Tight | 0.84 | 0.52 | 0.38 | 0.31 | 0.27 | 1.32 | 0.67 | 0.42 | 0.33 | 0.2 | 0.59 | 0.4 | 0.31 | 0.27 | 0.23 | 0.76 | 0.42 | 0.28 | 0.23 | 0.18
Tight | 0.37 | 0.23 | 0.17 | 0.14 | 0.12 | 0.59 | 0.3 | 0.19 | 0.15 | 0.09 | 0.26 | 0.18 | 0.14 | 0.12 | 0.1 | 0.34 | 0.19 | 0.12 | 0.1 | 0.08
| 5C11 | 5C12 | 5C13 | 5C14 | 5C15 | 5C21 | 5C22 | 5C23 | 5C24 | 5C25 | 5D11 | 5D12 | 5D13 | 5D14 | 5D15 | 5D21 | 5D22 | 5D23 | 5D24 | 5D25
Average | 0.69 | 0.42 | 0.31 | 0.26 | 0.22 | 1.08 | 0.55 | 0.34 | 0.27 | 0.16 | 0.48 | 0.33 | 0.26 | 0.22 | 0.19 | 0.62 | 0.34 | 0.23 | 0.19 | 0.15
Loose | 1.18 | 0.73 | 0.53 | 0.44 | 0.37 | 1.85 | 0.94 | 0.59 | 0.47 | 0.27 | 0.82 | 0.56 | 0.44 | 0.38 | 0.32 | 1.06 | 0.59 | 0.39 | 0.32 | 0.26
Average | 0.94 | 0.58 | 0.42 | 0.35 | 0.3 | 1.47 | 0.75 | 0.47 | 0.37 | 0.22 | 0.65 | 0.45 | 0.35 | 0.3 | 0.26 | 0.84 | 0.47 | 0.31 | 0.25 | 0.2
Semi-Loose | 0.44 | 0.27 | 0.2 | 0.17 | 0.14 | 0.7 | 0.35 | 0.22 | 0.17 | 0.1 | 0.31 | 0.21 | 0.16 | 0.14 | 0.12 | 0.4 | 0.22 | 0.15 | 0.12 | 0.1
Tight | 0.2 | 0.12 | 0.09 | 0.07 | 0.06 | 0.31 | 0.16 | 0.1 | 0.08 | 0.05 | 0.14 | 0.09 | 0.07 | 0.06 | 0.05 | 0.18 | 0.1 | 0.07 | 0.05 | 0.04
Occupant Activity | 5C14: Sensible; 5C15: Latent
Athletics, civilian intensity | 5C14: 710; 5C15: 1090
Athletics, moderate intensity | 5C14: 1000; 5C15: 1500
Athletics, extreme intensity | 5C14: 2000; 5C15: 3000
Audience, seated at rest | 5C14: 290; 5C15: 125
Audience, movement | 5C14: 300; 5C15: 550
Bowling | 5C14: 580; 5C15: 870
Workstation, seated no movement | 5C14: 275; 5C15: 475
Workstation, moderate movement | 5C14: 305; 5C15: 545
Workstation, extreme movement | 5C14: 565; 5C15: 1035
Dancing, moderate | 5C14: 305; 5C15: 545
Dancing, vigorously | 5C14: 710; 5C15: 1090
Factory work, movement, no lifting | 5C14: 375; 5C15: 625
Factory work, movement, lifting | 5C14: 580; 5C15: 870
Seated, bar or conference room | 5C14: 245; 5C15: 155
Seated, desk, body movement | 5C14: 250; 5C15: 200
Seated, eating a meal | 5C14: 275; 5C15: 275
Standing, some movement | 5C14: 250; 5C15: 200
Standing, light work | 5C14: 275; 5C15: 475
Standing | 5C14: 250; 5C15: 200
Walking briskley | 5C14: 375; 5C15: 625
Walking slowly | 5C14: 315; 5C15: 325
Blower Load
Draw Thru Blower | 5C11: 0.05
Blow Thru Blower | 5C11: 0.05
Return Fan | 5C11: 0.025
Ventilation
Air Changes/Hour | 5C11: 2
Occupants | 5C11: 3
Code CFM | 5C11: 4
15
20
30

## Cities (hidden)
Location | Elevation | Latitude | 99%db | 1% db | wb | 55 | 50 | 45 | DR |  | Alabama | California | Alabama | Alaska | Arizona | Arkansas | California | Colorado | Connecticut | Delaware | District of Columbia | Florida | Georgia | Hawaii | Idaho | Illinois | Indiana | Iowa | Kansas | Kentucky | Louisiana | Maine | Maryland | Massachusetts | Michigan | Minnesota | Mississippi | Missouri | Montana | Nebraska | Nevada | New Hampshire | New Jersey | New Mexico | New York | North Carolina | North Dakota | Ohio | Oklahoma | Oregon | Pennsylvania | Rhode Island | South Carolina | South Dakota | Tennessee | Texas | Utah | Vermont | Virginia | Washington | West Virginia | Wisconsin | Wyoming
California, Long Beach Daughtery Field | 39 | 34 | 44 | 88 | 67 | -4 | 3 | 9 | M | 2 | Alaska | Alameda, NAS | Alexander City | Adak, NAS | Douglas AP | Blytheville AFB | Alameda, NAS | Alamosa AP | Bridgeport AP | Dover AFB | Andrews AFB | Apalachicola | Albany, Turner | Ewa, Barbers Point NAS | Boise AP | Aurora | Anderson | Ames | Atchison | Ashland | Alexandria AP | Augusta AP | Balitimore AP | Boston AP | Adrian 798 | Albert Lea | Biloxi, Keesler AFB | Cape Girardeau | Billings AP | Beatrice | Carson City | Berlin | Atlantic City CO | Alamagordo Holloman AFB | Albany AP | Asheville AP | Bismark AP | Akron-Canton AP | Ada | Albany | Allentown AP | Newport | Anderson | Aberdeen AP | Athens | Abilene AP | Cedar City AP | Barre | Charlottsville | Aberdeen | Beckley | Appleton | Big Piney
Database | [9 empty] | 3 | Arizona | Bakersfield AP | Anniston AP | Anchorage IAP | Flagstaff Ap | Camden | Bakersfield AP | Boulder | Hartford, Brainard Field | Wilmington AP | Reagan National AP | Belle Glade | Americus | Hilo AP | Burley | Belleville, Scott AFB | Bedford | Burlington AP | Chante AP | Bowling Green AP | Baton Rouge AP | Bangor, Dow AFB | Balitimore CO | Clinton | Alpena AP | Alexandria AP | Clarksdale | Columbia AP | Bozeman | Bellevue, Offutt AFB | Elko AP | Claremont | Long Branch | Albuquerque AP | Albany CO | Cape Hatteras | Devil’s Lake | Ashtabula | Altus AFB | Astoria AP | Altoona CO | Providence AP | Beaufort, MCAS | Brookings | Bristol-Tri City AP | Alice AP | Logan | Burlington AP | Danville AP | Bellingham AP | Bluefield AP | Ashland | Casper AP
Alabama, Alexander City | 686 | 33 | 22 | 93 | 76 | 39 | 46 | 52 | M | 4 | Arkansas | Barstow | Auburn | Anchorage, Elemendorf AFB | Fort Huachuca AP | El Dorado AP | Barstow | Colarado Springs AP | New Haven AP |  |  | Cape Kennedy AP | Athens | Honolulu AP | Coeur D’Alene AP | Bloomington | Bloomington | Cedar Rapids AP | Concordia | Corbin AP | Bogalusa | Brunswick, NAS | Cumberland | East Falmouth, Otis ANGB | Battle Creek AP | Bemidji AP | Columbus AFB | Farmington AP | Butte AP | Chadron AP | Ely AP | Concord AP | Millville | Artesia | Auburn | Charlotte AP | Dickinson AP | Athens | Ardmore | Baker AP | Bradford |  | Charleston AFB | Chamberlain | Chattanooga AP | Amarillo AP | Moab | Montpelier/ Barre | Fort Belvoir | Bremerton | Charleston AP | Beloit | Cheyene AP
Alabama, Anniston AP | 612 | 33 | 24 | 93 | 76 | 39 | 46 | 52 | M | 5 | California | Blue Canyon | Birmingham AP | Anchorage, Fort Richardson | Kingman AP | Fayetteville AP | Blue Canyon | Craig | New London |  |  | Daytona Beach AP | Atlanta AP | Kahului | Idaho Falls AP | Carbondale | Columbus, Bakalar AFB | Clinton | Dodge City AP | Covington AP | Bossier City, Barksdale AFB | Caribou AP | Fredrick AP | Fall River | Benton Harbor AP | Brainerd | Greenville AFB | Hannibal | Cut Bank AP | Columbus | Las Vegas AP | Keene | Newark AP | Carlsbad AP | Bafavia | Cherry Point MCAS | Fargo AP | Bowling Green | Bartlesville | Bend | Butler |  | Charleston CO | Huron AP | Clarksville | Austin AP | Ogden, Hill AFB | Rutland | Fredricksburg | Ellensburg AP | Clarksburg | Eau Claire AP | Cody AP
Alabama, Auburn | 776 | 32 | 22 | 93 | 76 | 39 | 46 | 52 | M | 6 | Colorado | Blythe AP | Decatur | Annette | Nogalas | Fort Smith AP | Blythe AP | Denver AP | Norwalk |  |  | Fort Lauderdale | Augusta AP | Kaneohe Bay MCAS | Kamiah | Champaign/Urbana | Crawfordsville | Council Bluffs | El Dorado | Fort Knox, Godman AAF | Houma | Lewiston | Hagerstown | Framingham | Detroit | Duluth AP | Greenwood | Jefferson City | Glasgow AP | Fremont | Lovelock AP | Laconia | New Brunswick | Clayton | Binghampton AP | Durham | Grands Forks AP | Cambridge | Chickasha | Corvallis | Chambersburg |  | Columbia AP | Mitchell | Columbia | Bay City | Price |  | Hampton, Langley AFB | Everett-Paine AFB | Elkins AP | Fond du Lac | Evanston
Alabama, Birmingham AP | 644 | 33 | 23 | 92 | 75 | 34 | 41 | 47 | M | 7 | Connecticut | Burbank AP | Dothan AP | Barrow | Page | Hot Springs | Burbank AP | Durango | Norwich |  |  | Fort Myers AP | Brunswick | Lihue | Lewiston AP | Chicago, Meigs Field | Evansville AP | Des Moines AP | Emporia | Hopkinsville, Campbell AFB | Lafayette AP | Limestone, Loring AFB | Lex Park, Patuxent River NAS | Gloucester | Escanaba | Fairbault | Hattiesburg | Joplin AP | Glendive | Grand Island AP | Mercury | Lebanon | Patterson | Clovis, Cannon AFB | Buffalo AP | Elizabeth City AP | Jamestown AP | Chilicothe | Enid-Vance AFB | Eugene AP | DuBois |  | Florence AP | Pierre AP | Crossville | Beaumont | Provo |  | Harrisonburg | Hanford | Huntington CO | Green Bay AP | Gillette
Alabama, Decatur | 592 | 34 | 16 | 93 | 74 | 27 | 34 | 40 | M | 8 | Delaware | Chico | Florence AP | Bethel | Phoenix AP | Jonesboro 262 | Chico | Eagle | Waterbury |  |  | Fort Pierce | Columbus, Fort Benning | Molokai | Moscow | Chicago, Midway AP | Fort Wayne AP | Debuque | Garden City AP | Jackson | Lake Charles AP | Millinocket AP | Salisbury | Greenfield | Flint AP | Fergus Falls | Jackson AP | Kansas City AP | Great Falls AP | Hastings | North Las Vega , Nellis AFB | Manchester, Grenier AFB | Phillipsburg | Farmington AP | Central Islip | Fayetteville, Pope AFB | Minot AP | Cincinnati, Lunken Field | Lawton AP | Grants Pass | Erie AP |  | Georgetown | Rapid City AP | Dyersburg | Beeville | Richfield |  | Lynchburg AP | Kennewick | Martinsburg AP | LaCrosse AP | Lander AP
Alabama, Dothan AP | 401 | 31 | 32 | 93 | 76 | 39 | 46 | 52 | M | 9 | District of Columbia | Concord | Gadsden | Bettles | Phoenix, Luke AFB | Little Rock AP | Concord | Fort Collins | Windsor Locks, Bradlet Field |  |  | Gainsville AP | Columbus, Lawson AFB | Wahaiwa | Mountain Home AFB | Chicago, O’Hare AP | Goshen AP | Fort Dodge | Goodland AP | Lexington AP | Leesville, Fort Polk | Portland |  | Lawrence | Grand Rapids AP | Hibbing | Laurel | Kirksville AP | Great Falls, Malmstrom AFB | Kearney | Reno AP | Mount Washington | Teterboro | Gallup | Cortland | Goldsboro, Seymour | Minot, AFB | Cleveland AP | McAlester | Hillsboro | Harrisburg AP |  | Greenville AP/Greer | Sioux Falls AP | Greenville | Big Springs AP | St. George CO |  | Newport News | Longview | Morgantown AP | Madison AP | Laramie AP
Alabama, Florence AP | 581 | 34 | 21 | 94 | 75 | 31 | 38 | 44 | M | 10 | Florida | Covina | Huntsville AP | Big Delta, Ft. Greely | Prescott AP | Pine Bluff AP | Covina | Grand Junction AP |  |  |  | Homestead, AFB | Columbus, Metro AP |  | Mullan | Chicago CO | Hobart | Iowa City | Great Bend | Louisville AP | Minden | Waterville |  | Lowell | Hancock | International Falls AP | McComb AP | Mexico | Havre | Lincoln CO | Reno CO | Portsmouth, Pease AFB | Trenton, McQuire AFB | Grants | Dunkirk | Goldsboro, Johnson AFB | Williston | Columbus AP | Muskogee AP | Klamath Falls AP | Johnstown |  | Greenwood | Watertown AP | Jackson AP | Brownsville AP | Salt Lake City AP |  | Norfolk AP | Moses Lake, Larson AFB | Parkersburg CO | Manitowoc | Newcastle
Alabama, Gadsden | 569 | 34 | 20 | 94 | 75 | 31 | 38 | 44 | M | 11 | Georgia | Crescent City AP | Mobile AP | Cold Bay | Safford, Agri. Center | Texarkana AP | Crescent City AP | Greeley |  |  |  | Jacksonville AP | Dalton |  | Pocatello AP | Danville | Huntington | Keokuk | Hutchinson AP | Madisonville | Monroe AP |  |  | New Bedford | Harbour Beach | Mankato 1020 | Meridian AP | Moberly | Helena AP | McCook | Tonapah AP |  | Vineland | Hobbs AP | Elmira AP | Greensboro AP |  | Columbus, Rickenbckr AFB | Norman 1181 | Meacham | Lancaster |  | Myrtle Beach, AFB | Yankton | Knoxville AP | Brownwood | Vernal AP |  | Oceana, NAS | Olympia AP | Wheeling | Marinette | Rawlins
Alabama, Huntsville AP | 629 | 34 | 20 | 92 | 74 | 28 | 35 | 41 | M | 12 | Hawaii | Downey | Mobile CO | Cordova | Tuscon Ap |  | Downey | LaJunta AP |  |  |  | Jacksonville/Cecil Field NAS | Dublin |  | Twin Falls AP | Decatur | Indianapolis AP (S) | Lamoni | Liberal | Owensboro | Natchitoches |  |  | Pittsfield AP | Holland | Minneapolis/St. Paul AP | Natchez | Poplar Bluff | Kalispell AP | Norfolk | Winnemucca AP |  |  | Las Cruces | Geneva | Greenville |  | Dayton AP | Oklahoma City AP | Medford AP | Meadville |  | Orangeburg |  | Memphis AP | Bryan AP |  |  | Petersburg | Port Angeles |  | Milwaukee AP | Rock Springs AP
Alabama, Mobile AP | 218 | 30 | 30 | 92 | 76 | 41 | 48 | 54 | M | 13 | Idaho | El Cajon | Montgomery AP | Deadhorse | Winslow AP |  | El Cajon | Leadville |  |  |  | Jacksonville, Mayport Naval | Gainesville |  |  | Dixon | Jeffersonville | Marshalltown | Manhattan, Fort Riley | Paducah AP | New Orleans AP |  |  | Springfield, Westover AFB | Jackson AP | Redwood Falls | Tupelo | Rolla | Lewiston AP | North Platte AP |  |  |  | Los Alamos | Glens Falls | Henderson |  | Dayton, Wright/Paterson AFB | Oklahoma City, W.Rogers AP | North Bend | New Castle |  | Rock Hill |  | Murfreesboro | Corpus Christi AP |  |  | Quantico MCAS | Quillayute |  | Racine | Sheridan AP
Alabama, Mobile CO | 26 | 30 | 29 | 93 | 77 | 46 | 53 | 59 | M | 14 | Illinois | El Centro AP | Ozark, Fort Rucker | Dillingham | Yuma AP |  | El Centro AP | Limon |  |  |  | Key West AP | Griffin |  |  | Elgin | Kokoma | Mason City AP | Parsons |  | New Orleans, Lakefront AP |  |  | Tauton | Kalamazoo | Rochester AP | Vicksburg CO | St. Joseph AP | Livingston AP | Omaha AP |  |  |  | Raton AP | Gloversville | Hickory |  | Defiance | Ponca City | Pendleton AP | Philadelphia AP |  | Spartanburg AP |  | Nashville AP | Corsicana |  |  | Richmond AP | Seattle-Boeing Fld |  | Sheboygan | Torrington
Alabama, Montgomery AP | 221 | 32 | 27 | 93 | 76 | 39 | 46 | 52 | M | 15 | Indiana | Escondido | Selma-Craig AFB | Fairbanks IAP |  |  | Escondido | Pueblo AP |  |  |  | Lakeland CO | La Grange |  |  | Freeport | Layfayette | Newton | Russel AP |  | Shreveport AP |  |  | Weymouth, S. Weymouth Nas | Lansing AP | St. Cloud AP |  | St. Louis AP | Miles City AP | Omaha WSO |  |  |  | Roswell, Walker AFB | Hornell | Jacksonville |  | Finlay AP | Seminole | Portland AP | Philadelphia, Northeast AP |  | Sumter-Shaw AFB |  | Tullahoma | Dallas, Fort Worth AP |  |  | Roanoke AP | Seattle CO |  | Stevens Point | Worland
Alabama, Ozark, Fort Rucker | 356 | 31 | 31 | 94 | 77 | 44 | 51 | 57 | M | 16 | Iowa | Eureaka/Arcata AP | Talladega | Fairbanks, Eielson AFB |  |  | Eureaka/Arcata AP | Sterling |  |  |  | Melbourne | Macon AP |  |  | Galesburg | LaPorte | Ottumwa AP | Salina |  |  |  |  | Worcester AP | Marquette CO | Tofte |  | St. Louis CO | Missoula AP | Scottsbluff AP |  |  |  | Santa Fe CO | Ithaca | Lumberton |  | Fremont | Stillwater | Portland CO | Philadelphia, Willow Gr NAS |  |  |  |  | Del Rio, Laughlin AFB |  |  | Staunton | Seattle-Tacoma AP |  | Waukesha
Alabama, Selma-Craig AFB | 166 | 32 | 26 | 95 | 77 | 42 | 49 | 55 | M | 17 | Kansas | Fairfield-Travis AFB | Tuscaloosa AP | Galena |  |  | Fairfield-Travis AFB | Trinidad AP |  |  |  | Miami AP | Marietta, Dobbins AFB |  |  | Glenview, NAS | Marion | Sioux City AP | Topeka AP | [5 empty] | Marquette, Sawyer AFB | Virginia |  | Sedalia, Whiteman AFB |  | Sidney AP |  |  |  | Silver City AP | Jamestown | New Bern AP |  | Hamilton | Tulsa AP | Redmond | Pittsburgh AP |  |  |  |  | Denton |  |  | Sterling | Spokane AP |  | Wausau AP
Alabama, Talladega | 528 | 33 | 22 | 94 | 76 | 37 | 44 | 50 | M | 18 | Kentucky | Fresno AP |  | Gulkana |  |  | Fresno AP |  |  |  |  | Miami CO | Moultrie |  |  | Greenville | Muncie | Spencer | Wichita AP | [5 empty] | Mount Clemens ANGB | Willmar |  | Sikeston |  | Valentine |  |  |  | Socorro AP | Kingston | Raleigh/Durham AP |  | Lancaster | Woodward | Roseburg AP | Pittsburgh, Allegheny AP |  |  |  |  | Eagle Pass |  |  | Reagan, National AP | Stampede Pass
Alabama, Tuscaloosa AP | 170 | 33 | 24 | 94 | 77 | 44 | 51 | 57 | M | 19 | Louisiana | Hamiltion AFB |  | Homer |  |  | Hamiltion AFB |  |  |  |  | Miami, New Tamiami AP | Rome AP |  |  | Joliet | Peru, Bunker Hill AFB | Waterloo | Wichita, McConnell AFB | [5 empty] | Mt. Pleasant | Winona |  | Spickard/Trenton | [5 empty] | Truth or Consequences | Lockport | Rocky Mount |  | Lima |  | Salem AP | Reading CO |  |  |  |  | El Paso AP |  |  | Winchester | Tacoma-McChord AFB
Alaska, Adak, NAS | 19 | 52 | 23 | 57 | 53 | -18 | -11 | -5 | L | 20 | Maine | Laguna Beach |  | Juneau IAP |  |  | Laguna Beach |  |  |  |  | Milton, Whiting Field NAS | Savannah, Travis AP |  |  | Kankakee | Peru, Grsssom AFB | [7 empty] | Muskegon AP |  |  | Springfield AP | [5 empty] | Tucumcari AP | Massena AP | Wilmington AP |  | Mansfield AP |  | Sexton Summit | Scranton/Wilkes-Barre |  |  |  |  | Fort Worth, Carswell AFB |  |  |  | Walla Walla AP
Alaska, Anchorage IAP | 144 | 61 | -9 | 68 | 57 | -20 | -13 | -7 | L | 21 | Maryland | Lemoore, Reeves NAS |  | Kenai |  |  | Lemoore, Reeves NAS |  |  |  |  | Ocala | Valdosta, Moody AFB |  |  | LaSalle/Peru | Richmond AP | [7 empty] | Oscoda, Wurtsmith AFB |  |  | Warrensburg, Whiteman AFB | [6 empty] | Newburg-Stewart AFB | Winston-Salem AP |  | Marion |  | The Dalles | State College |  |  |  |  | Fort Worth, Meacham Field |  |  |  | Wenatchee
Alaska, Anchorage, Elemendorf AFB | 212 | 61 | -8 | 69 | 57 | -21 | -14 | -8 | L | 22 | Massachusetts | Livermore 500 |  | Ketchikan IAP |  |  | Livermore 500 |  |  |  |  | Orlando AP | Valdosta, Regional AP |  |  | Macomb | Shelbyville | [7 empty] | Pellston | [9 empty] | NYC-Central Park |  |  | Middletown |  |  | Sunbury |  |  |  |  | Galveston AP |  |  |  | Yakima AP
Alaska, Anchorage, Fort Richardson | 342 | 61 | -13 | 71 | 58 | -20 | -13 | -7 | M | 23 | Michigan | Lompoc, Vandenburg AFB |  | King Salmon |  |  | Lompoc, Vandenburg AFB |  |  |  |  | Panama City, Tyndall AFB | Waycross |  |  | Marseilles | South Bend AP | [7 empty] | Pontiac | [9 empty] | NYC-Kennedy AP |  |  | Newark |  |  | Uniontown |  |  |  |  | Greenville
Alaska, Annette | 110 | 55 | 17 | 70 | 59 | -14 | -7 | -1 | L | 24 | Minnesota | Long Beach Daughtery Field |  | Kodiak |  |  | Long Beach Daughtery Field |  |  |  |  | Pensacola CO |  |  |  | Moline, Davenport AP | Terre Haute AP | [7 empty] | Port Huron | [9 empty] | NYC-La Guardia AP |  |  | Norwalk |  |  | Warren |  |  |  |  | Guadalupe Pass
Alaska, Barrow | 44 | 71 | 36 | 52 | 49 | -25 | -18 | -12 | L | 25 | Mississippi | Los Angeles AP |  | Kotzebue |  |  | Los Angeles AP |  |  |  |  | St. Augustine |  |  |  | Mt. Vernon | Valparaiso | [7 empty] | Saginaw AP | [9 empty] | Niagra Falls AP |  |  | Portsmouth |  |  | West Chester |  |  |  |  | Harlingen
Alaska, Bethel | 123 | 61 | -24 | 68 | 57 | -20 | -13 | -7 | M | 26 | Missouri | Los Angeles CO |  | McGrath |  |  | Los Angeles CO |  |  |  |  | St. Petersburg |  |  |  | Peoria AP | Vincennes | [7 empty] | Sault Ste. Marie AP | [9 empty] | Olean |  |  | Sandusky CO |  |  | Williamsport AP |  |  |  |  | Houston AP
Alaska, Bettles | 643 | 67 | -44 | 75 | 59 | -22 | -15 | -9 | M | 27 | Montana | Marysville, Beale AFB |  | Middleton Island |  |  | Marysville, Beale AFB |  |  |  |  | Sanford |  |  |  | Quincy AP | [8 empty] | Seul Choix Point | [9 empty] | Oneonta |  |  | Springfield |  |  | York |  |  |  |  | Houston, Hobby AP
Alaska, Big Delta, Ft. Greely | 1277 | 64 | -39 | 75 | 58 | -27 | -20 | -14 | M | 28 | Nebraska | Merced-Castle AFB |  | Nenana |  |  | Merced-Castle AFB |  |  |  |  | Sarasota/Bradenton |  |  |  | Rantoul, Chanute AFB | [8 empty] | Traverse City AP | [9 empty] | Oswego CO |  |  | Stubenville | [7 empty] | Huntsville
Alaska, Cold Bay | 98 | 55 | 10 | 57 | 53 | -18 | -11 | -5 | L | 29 | Nevada | Modesto |  | Nome AP |  |  | Modesto |  |  |  |  | Tallahassee AP |  |  |  | Rockford | [8 empty] | Yipsilanti | [9 empty] | Plattsburg AFB |  |  | Toledo AP | [7 empty] | Junction
Alaska, Cordova | 42 | 60 | 1 | 67 | 57 | -18 | -11 | -5 | M | 30 | New Hampshire | Monterey |  | Northway |  |  | Monterey |  |  |  |  | Tampa AP |  |  |  | Springfield AP | [18 empty] | Poughkeepsie |  |  | Warren | [7 empty] | Killeen-Gray AFB
Alaska, Deadhorse | 61 | 70 | -34 | 61 | 54 | -21 | -14 | -8 | M | 31 | New Jersey | Mount Shasta |  | Port Heiden |  |  | Mount Shasta |  |  |  |  | Valpariso, Eglin AFB |  |  |  | Waukegan | [18 empty] | Rochester AP |  |  | Wooster | [7 empty] | Kingsville, NAS
Alaska, Dillingham | 86 | 59 | -13 | 66 | 56 | -21 | -14 | -8 | M | 32 | New Mexico | Mountain View, Moffet NAS |  | Saint Paul Island |  |  | Mountain View, Moffet NAS |  |  |  |  | Vero Beach |  |  |  | West Chicago | [18 empty] | Rome-Griffiss AFB |  |  | Youngstown AP | [7 empty] | Lamesa
Alaska, Fairbanks IAP | 434 | 64 | -41 | 77 | 59 | -26 | -19 | -13 | M | 33 | New York | Napa |  | Sitka |  |  | Napa |  |  |  |  | West Palm Beach AP | [22 empty] | Schenectady |  |  | Zanesville AP | [7 empty] | Laredo AFB
Alaska, Fairbanks, Eielson AFB | 545 | 64 | -31 | 78 | 60 | -23 | -16 | -10 | M | 34 | North Carolina | Needles AP |  | Talkeetna |  |  | Needles AP | [27 empty] | Suffolk County AFB | [10 empty] | Longview 365
Alaska, Galena | 152 | 64 | -31 | 74 | 59 | -21 | -14 | -8 | M | 35 | North Dakota | Oakland AP |  | Valdez |  |  | Oakland AP | [27 empty] | Syracuse AP | [10 empty] | Lubbock AP
Alaska, Gulkana | 1579 | 62 | -39 | 73 | 56 | -32 | -25 | -19 | M | 36 | Ohio | Oceanside |  | Yakutat |  |  | Oceanside | [27 empty] | Utica | [10 empty] | Lubbock, Reese AFB
Alaska, Homer | 78 | 59 | 4 | 62 | 55 | -18 | -11 | -5 | L | 37 | Oklahoma | Ontario IAP |  |  |  |  | Ontario IAP | [27 empty] | Watertown | [10 empty] | Lufkin AP
Alaska, Juneau IAP | 19 | 58 | 7 | 69 | 58 | -17 | -10 | -4 | L | 38 | Oregon | Oxnard |  |  |  |  | Oxnard | [27 empty] | White Plains | [10 empty] | Marfa
Alaska, Kenai | 92 | 60 | -14 | 65 | 55 | -23 | -16 | -10 | M | 39 | Pennsylvania | Palmdale AP |  |  |  |  | Palmdale AP | [38 empty] | McAllen
Alaska, Ketchikan IAP | 88 | 55 | 20 | 68 | 59 | -11 | -4 | 2 | L | 40 | Rhode Island | Palm Springs |  |  |  |  | Palm Springs | [38 empty] | Midland AP
Alaska, King Salmon | 57 | 58 | -19 | 67 | 56 | -22 | -15 | -9 | M | 41 | South Carolina | Pasadena |  |  |  |  | Pasadena | [38 empty] | Mineral Wells AP
Alaska, Kodiak | 73 | 57 | 12 | 65 | 56 | -19 | -12 | -6 | L | 42 | South Dakota | Paso Robles |  |  |  |  | Paso Robles | [38 empty] | Palestine CO
Alaska, Kotzebue | 11 | 66 | -31 | 64 | 58 | -9 | -2 | 4 | L | 43 | Tennessee | Petaluma |  |  |  |  | Petaluma | [38 empty] | Pampa
Alaska, McGrath | 337 | 62 | -42 | 73 | 58 | -23 | -16 | -10 | M | 44 | Texas | Pomona CO |  |  |  |  | Pomona CO | [38 empty] | Pecos
Alaska, Middleton Island | 87 | 59 | 21 | 60 | 51 | -31 | -24 | -18 | L | 45 | Utah | Red Bluff |  |  |  |  | Red Bluff | [38 empty] | Plainview
Alaska, Nenana | 362 | 64 | -44 | 76 | 59 | -24 | -17 | -11 | M | 46 | Vermont | Redding AP |  |  |  |  | Redding AP | [38 empty] | Port Arthur AP
Alaska, Nome AP | 37 | 64 | -26 | 65 | 55 | -23 | -16 | -10 | L | 47 | Virginia | Redlands |  |  |  |  | Redlands | [38 empty] | San Angelo, Goodfellow AFB
Alaska, Northway | 1716 | 62 | -32 | 74 | 57 | -29 | -22 | -16 | M | 48 | Washington | Richmond |  |  |  |  | Richmond | [38 empty] | San Antonio AP
Alaska, Port Heiden | 105 | 56 | -2 | 61 | 52 | -29 | -22 | -16 | L | 49 | West Virginia | Riverside-March AFB |  |  |  |  | Riverside-March AFB | [38 empty] | San Antonio, Kelly AFB
Alaska, Saint Paul Island | 63 | 57 | 3 | 52 | 50 | -22 | -15 | -9 | L | 50 | Wisconsin | Sacramento AP |  |  |  |  | Sacramento AP | [38 empty] | San Antonio, Randolph AFB
Alaska, Sitka | 21 | 57 | 21 | 64 | 58 | -9 | -2 | 4 | L | 51 | Wyoming | Sacramento, McClellan AFB |  |  |  |  | Sacramento, McClellan AFB | [38 empty] | Sanderson
Alaska, Talkeetna | 358 | 62 | -21 | 73 | 58 | -23 | -16 | -10 | M | 52 |  | Sacramento, Metro |  |  |  |  | Sacramento, Metro | [38 empty] | Sherman-Perrin AFB
Alaska, Valdez | 120 | 61 | 7 | 66 | 55 | -25 | -18 | -12 | L | 53 |  | Salinas AP |  |  |  |  | Salinas AP | [38 empty] | Snyder
Alaska, Yakutat | 33 | 59 | 2 | 63 | 55 | -20 | -13 | -7 | L | 54 |  | San Bernadino, Norton AFB |  |  |  |  | San Bernadino, Norton AFB | [38 empty] | Temple
Arizona, Douglas AP | 4173 | 31 | 31 | 95 | 63 | -34 | -27 | -21 | H | 55 |  | San Diego AP |  |  |  |  | San Diego AP | [38 empty] | Tyler AP
Arizona, Flagstaff Ap | 7011 | 35 | 8 | 83 | 55 | -54 | -47 | -41 | H | 56 |  | San Diego, Miramar NAS |  |  |  |  | San Diego, Miramar NAS | [38 empty] | Vernon
Arizona, Fort Huachuca AP | 4716 | 31 | 28 | 92 | 62 | -34 | -27 | -21 | H | 57 |  | San Fernando |  |  |  |  | San Fernando | [38 empty] | Victoria AP
Arizona, Kingman AP | 3446 | 35 | 27 | 97 | 63 | -38 | -31 | -25 | H | 58 |  | San Francisco AP |  |  |  |  | San Francisco AP | [38 empty] | Waco AP
Arizona, Nogalas | 3932 | 31 | 32 | 96 | 64 | -32 | -25 | -19 | H | 59 |  | San Francisco CO |  |  |  |  | San Francisco CO | [38 empty] | Wichita Falls AP
Arizona, Page | 4310 | 36 | 24 | 97 | 62 | -43 | -36 | -30 | H | 60 |  | San Jose AP |  |  |  |  | San Jose AP
Arizona, Phoenix AP | 1133 | 33 | 37 | 108 | 70 | -21 | -14 | -8 | H | 61 |  | San Luis Obispo |  |  |  |  | San Luis Obispo
Arizona, Phoenix, Luke AFB | 1101 | 33 | 38 | 107 | 71 | -14 | -7 | -1 | H | 62 |  | Santa Ana AP |  |  |  |  | Santa Ana AP
Arizona, Prescott AP | 5042 | 34 | 20 | 91 | 60 | -42 | -35 | -29 | H | 63 |  | Santa Barbara AP |  |  |  |  | Santa Barbara AP
Arizona, Safford, Agri. Center | 3176 | 32 | 26 | 99 | 66 | -25 | -18 | -12 | H | 64 |  | Santa Cruz |  |  |  |  | Santa Cruz
Arizona, Tuscon Ap | 2641 | 32 | 24 | 102 | 65 | -39 | -30 | -24 | H | 65 |  | Santa Maria AP |  |  |  |  | Santa Maria AP
Arizona, Winslow AP | 4938 | 35 | 14 | 93 | 60 | -46 | -39 | -33 | H | 66 |  | Santa Monica CO |  |  |  |  | Santa Monica CO
Arizona, Yuma AP | 213 | 32 | 44 | 109 | 72 | -15 | -8 | -2 | H | 67 |  | Santa Paula |  |  |  |  | Santa Paula
Arkansas, Blytheville AFB | 264 | 36 | 18 | 95 | 77 | 42 | 49 | 55 | M | 68 |  | Santa Rosa |  |  |  |  | Santa Rosa
Arkansas, Camden | 130 | 33 | 23 | 96 | 76 | 34 | 41 | 47 | M | 69 |  | Stockton AP |  |  |  |  | Stockton AP
Arkansas, El Dorado AP | 277 | 33 | 23 | 96 | 76 | 34 | 41 | 47 | M | 70 |  | Ukiah |  |  |  |  | Ukiah
Arkansas, Fayetteville AP | 1251 | 36 | 13 | 93 | 75 | 33 | 40 | 46 | M | 71 |  | Victorville, George AFB |  |  |  |  | Victorville, George AFB
Arkansas, Fort Smith AP | 469 | 35 | 19 | 96 | 76 | 34 | 41 | 47 | M | 72 |  | Visalia |  |  |  |  | Visalia
Arkansas, Hot Springs | 540 | 34 | 23 | 97 | 77 | 39 | 46 | 52 | M | 73 |  | Yreka |  |  |  |  | Yreka
Arkansas, Jonesboro 262 | 35 | 15 | 94 | 77 | 44 | 51 | 57 | M |  | 74 |  | Yuba City |  |  |  |  | Yuba City
Arkansas, Little Rock AP | 260 | 34 | 21 | 95 | 77 | 42 | 49 | 55 | M
Arkansas, Pine Bluff AP | 206 | 34 | 22 | 97 | 77 | 39 | 46 | 52 | M
Arkansas, Texarkana AP | 389 | 33 | 25 | 95 | 77 | 42 | 49 | 55 | M
California, Alameda, NAS | 15 | 37 | 42 | 79 | 64 | -6 | 1 | 7 | M
California, Bakersfield AP | 507 | 35 | 35 | 101 | 69 | -15 | -8 | -2 | H
California, Barstow | 1927 | 34 | 32 | 105 | 67 | -32 | -25 | -19 | H
California, Blue Canyon | 5280 | 39 | 24 | 81 | 57 | -41 | -34 | -28 | M
California, Blythe AP | 397 | 33 | 33 | 110 | 71 | -18 | -11 | -5 | H
California, Burbank AP | 775 | 34 | 41 | 95 | 69 | -6 | 1 | 7 | M
California, Chico | 238 | 39 | 30 | 101 | 68 | -22 | -15 | -9 | H
California, Concord | 23 | 38 | 27 | 97 | 68 | -14 | -7 | -1 | H
California, Covina | 575 | 34 | 35 | 95 | 68 | -11 | -5 | 2 | H
California, Crescent City AP | 57 | 41 | 33 | 65 | 59 | -6 | 1 | 7 | M
California, Downey | 110 | 34 | 40 | 89 | 70 | 9 | 15 | 22 | M
California, El Cajon | 387 | 32 | 44 | 80 | 69 | 19 | 26 | 32 | H
California, El Centro AP | -30 | 32 | 38 | 110 | 74 | -3 | 4 | 10 | H
California, Escondido | 660 | 33 | 41 | 85 | 68 | 5 | 12 | 18 | H
California, Eureaka/Arcata AP | 217 | 41 | 32 | 67 | 59 | -10 | -3 | 3 | L
California, Fairfield-Travis AFB | 62 | 38 | 34 | 94 | 67 | -15 | -8 | -2 | H
California, Fresno AP | 328 | 36 | 32 | 101 | 70 | -10 | -3 | 3 | H
California, Hamiltion AFB | 3 | 38 | 32 | 84 | 66 | -4 | 3 | 9 | H
California, Laguna Beach | 35 | 33 | 43 | 80 | 68 | 0 | 3 | 6 | M
California, Lemoore, Reeves NAS | 237 | 36 | 32 | 101 | 71 | -4 | 3 | 9 | H
California, Livermore 500 | 397 | 38 | 97 | 68 | -14 | -3 | 3 | 10 | H
California, Lompoc, Vandenburg AFB | 87 | 34 | 38 | 70 | 61 | -5 | 2 | 8 | M
California, Long Beach Daughtery Field | 39 | 34 | 44 | 88 | 67 | -4 | 3 | 9 | M
California, Los Angeles AP | 97 | 34 | 45 | 81 | 64 | -9 | -2 | 8 | L
California, Los Angeles CO | 270 | 34 | 40 | 89 | 70 | 10 | 17 | 23 | M
California, Marysville, Beale AFB | 119 | 39 | 34 | 98 | 69 | -10 | -3 | 3 | H
California, Merced-Castle AFB | 188 | 37 | 32 | 97 | 69 | -9 | -2 | 4 | H
California, Modesto | 97 | 37 | 30 | 98 | 68 | -16 | -9 | -3 | H
California, Monterey | 162 | 36 | 38 | 71 | 61 | -7 | 0 | 6 | M
California, Mount Shasta | 3543 | 41 | 21 | 88 | 61 | -33 | -26 | -20 | H
California, Mountain View, Moffet NAS | 34 | 37 | 39 | 84 | 65 | -9 | -2 | 4 | M
California, Napa | 33 | 38 | 32 | 96 | 68 | -12 | -5 | 1 | H
California, Needles AP | 983 | 34 | 33 | 110 | 71 | -18 | -11 | -5 | H
California, Oakland AP | 6 | 37 | 36 | 80 | 63 | -12 | -5 | 1 | M
California, Oceanside | 28 | 33 | 43 | 80 | 68 | 13 | 20 | 26 | L
California, Ontario IAP | 952 | 34 | 38 | 98 | 70 | -5 | 2 | 8 | H
California, Oxnard | 7 | 34 | 41 | 79 | 64 | -6 | 1 | 7 | M
California, Palmdale AP | 2542 | 34 | 24 | 98 | 65 | -31 | -24 | -18 | H
California, Palm Springs | 462 | 33 | 35 | 110 | 70 | -24 | -17 | -11 | H
California, Pasadena | 864 | 34 | 35 | 95 | 68 | -11 | -4 | 2 | H
California, Paso Robles | 837 | 35 | 29 | 98 | 67 | -21 | -14 | -8 | H
California, Petaluma | 87 | 38 | 29 | 90 | 66 | -13 | -6 | 0 | H
California, Pomona CO | 934 | 34 | 30 | 99 | 69 | -12 | -5 | 1 | H
California, Red Bluff | 342 | 40 | 32 | 102 | 69 | -17 | -10 | -4 | H
California, Redding AP | 502 | 40 | 31 | 102 | 67 | -27 | -20 | -14 | H
California, Redlands | 1571 | 34 | 33 | 99 | 69 | -12 | -5 | 1 | H
California, Richmond | 55 | 38 | 36 | 80 | 63 | -12 | -6 | 1 | M
California, Riverside-March AFB | 1533 | 33 | 36 | 98 | 68 | -16 | -9 | -3 | H
California, Sacramento AP | 95 | 38 | 32 | 97 | 68 | -14 | -7 | -1 | H
California, Sacramento, McClellan AFB | 75 | 38 | 34 | 98 | 67 | -21 | -14 | -8 | H
California, Sacramento, Metro | 23 | 38 | 33 | 97 | 69 | -9 | -2 | 4 | H
California, Salinas AP | 85 | 36 | 35 | 78 | 62 | -14 | -7 | -1 | M
California, San Bernadino, Norton AFB | 1156 | 34 | 36 | 101 | 70 | -10 | -3 | 3 | H
California, San Diego AP | 13 | 32 | 46 | 81 | 67 | 6 | 13 | 19 | L
California, San Diego, Miramar NAS | 477 | 32 | 42 | 88 | 67 | -5 | 2 | 8 | M
California, San Fernando | 977 | 34 | 39 | 91 | 68 | -4 | 2 | 9 | H
California, San Francisco AP | 8 | 37 | 39 | 78 | 62 | -14 | -7 | -1 | M
California, San Francisco CO | 20 | 37 | 40 | 71 | 62 | -2 | 5 | 11 | L
California, San Jose AP | 56 | 37 | 38 | 89 | 66 | -12 | -5 | 1 | H
California, San Luis Obispo | 250 | 35 | 35 | 88 | 70 | 11 | 18 | 24 | H
California, Santa Ana AP | 54 | 33 | 39 | 85 | 68 | 5 | 12 | 18 | H
California, Santa Barbara AP | 10 | 34 | 37 | 80 | 64 | -8 | 1 | 5 | M
California, Santa Cruz | 125 | 37 | 38 | 71 | 61 | -7 | 2 | 6 | H
California, Santa Maria AP | 240 | 34 | 35 | 82 | 62 | -20 | -13 | -7 | M
California, Santa Monica CO | 236 | 34 | 43 | 80 | 68 | 13 | 20 | 26 | M
California, Santa Paula | 245 | 34 | 35 | 86 | 67 | -2 | 5 | 11 | H
California, Santa Rosa | 125 | 38 | 29 | 95 | 67 | -16 | -9 | -3 | H
California, Stockton AP | 22 | 37 | 32 | 97 | 68 | -14 | -7 | -1 | H
California, Ukiah | 614 | 39 | 29 | 95 | 68 | -11 | -4 | 2 | H
California, Victorville, George AFB | 2875 | 34 | 30 | 98 | 65 | -31 | -24 | -18 | H
California, Visalia | 292 | 36 | 30 | 100 | 69 | -14 | -7 | -1 | H
California, Yreka | 2625 | 41 | 17 | 92 | 64 | -25 | -18 | -11 | H
California, Yuba City | 58 | 39 | 31 | 101 | 67 | -26 | -19 | -13 | H
Colorado, Alamosa AP | 7543 | 37 | -11 | 82 | 55 | -53 | -46 | -40 | H
Colorado, Boulder | 5385 | 40 | 0 | 91 | 59 | -47 | -40 | -34 | H
Colorado, Colarado Springs AP | 6171 | 38 | 4 | 87 | 58 | -46 | -39 | -33 | H
Colorado, Craig | 6283 | 40 | -12 | 85 | 56 | -52 | -45 | -39 | H
Colorado, Denver AP | 5283 | 39 | -3 | 90 | 59 | -46 | -39 | -33 | H
Colorado, Durango | 6684 | 37 | -1 | 87 | 59 | -41 | -34 | -28 | H
Colorado, Eagle | 6539 | 39 | -7 | 86 | 57 | -49 | -42 | -36 | H
Colorado, Fort Collins | 4935 | 40 | 1 | 91 | 59 | -48 | -41 | -35 | H
Colorado, Grand Junction AP | 4843 | 39 | 7 | 94 | 60 | -47 | -40 | -34 | H
Colorado, Greeley | 4820 | 40 | 4 | 94 | 60 | -47 | -40 | -34 | H
Colorado, LaJunta AP | 4238 | 38 | 3 | 98 | 68 | -11 | -4 | 2 | H
Colorado, Leadville | 9927 | 39 | -14 | 81 | 51 | -71 | -64 | -58 | H
Colorado, Limon | 5364 | 39 | 1 | 88 | 60 | -37 | -30 | -24 | H
Colorado, Pueblo AP | 4684 | 38 | 5 | 94 | 62 | -37 | -30 | -24 | H
Colorado, Sterling | 4038 | 40 | -2 | 93 | 62 | -36 | -29 | -23 | H
Colorado, Trinidad AP | 5761 | 37 | 6 | 90 | 60 | -40 | -33 | -27 | H
Connecticut, Bridgeport AP | 10 | 41 | 12 | 84 | 72 | 29 | 36 | 42 | M
Connecticut, Hartford, Brainard Field | 19 | 41 | 6 | 88 | 72 | 23 | 30 | 36 | M
Connecticut, New Haven AP | 14 | 41 | 7 | 84 | 73 | 35 | 42 | 48 | M
Connecticut, New London | 10 | 41 | 9 | 85 | 72 | 26 | 32 | 39 | M
Connecticut, Norwalk | 397 | 41 | 9 | 84 | 71 | 22 | 29 | 36 | M
Connecticut, Norwich | 197 | 41 | 7 | 86 | 73 | 30 | 37 | 44 | M
Connecticut, Waterbury | 850 | 41 | 2 | 85 | 71 | 22 | 29 | 35 | M
Connecticut, Windsor Locks, Bradlet Field | 197 | 42 | 8 | 88 | 71 | 16 | 22 | 29 | M
Delaware, Dover AFB | 28 | 39 | 18 | 89 | 75 | 39 | 46 | 52 | M
Delaware, Wilmington AP | 78 | 39 | 14 | 89 | 74 | 33 | 40 | 46 | M
District of Columbia, Andrews AFB | 283 | 38 | 18 | 91 | 74 | 30 | 37 | 43 | M
District of Columbia, Reagan National AP | 66 | 38 | 20 | 92 | 76 | 41 | 48 | 54 | M
Florida, Apalachicola | 20 | 29 | 35 | 90 | 78 | 57 | 64 | 70 | M
Florida, Belle Glade | 17 | 26 | 44 | 91 | 76 | 42 | 49 | 55 | M
Florida, Cape Kennedy AP | 10 | 28 | 42 | 90 | 78 | 57 | 64 | 70 | L
Florida, Daytona Beach AP | 31 | 29 | 37 | 90 | 77 | 51 | 58 | 64 | L
Florida, Fort Lauderdale | 10 | 26 | 50 | 90 | 78 | 57 | 64 | 70 | L
Florida, Fort Myers AP | 15 | 26 | 47 | 93 | 77 | 46 | 53 | 59 | M
Florida, Fort Pierce | 25 | 27 | 42 | 90 | 78 | 57 | 64 | 70 | M
Florida, Gainsville AP | 152 | 29 | 33 | 92 | 77 | 47 | 54 | 60 | M
Florida, Homestead, AFB | 7 | 25 | 52 | 90 | 78 | 57 | 64 | 70 | L
Florida, Jacksonville AP | 26 | 30 | 32 | 93 | 77 | 46 | 53 | 59 | M
Florida, Jacksonville/Cecil Field NAS | 80 | 30 | 34 | 95 | 76 | 36 | 43 | 49 | M
Florida, Jacksonville, Mayport Naval | 16 | 30 | 39 | 92 | 78 | 54 | 61 | 67 | M
Florida, Key West AP | 4 | 24 | 58 | 89 | 79 | 66 | 73 | 79 | L
Florida, Lakeland CO | 214 | 28 | 41 | 91 | 76 | 42 | 49 | 55 | M
Florida, Melbourne | 15 | 28 | 43 | 91 | 79 | 62 | 69 | 75 | M
Florida, Miami AP | 11 | 25 | 50 | 90 | 77 | 51 | 58 | 64 | L
Florida, Miami CO | 8 | 25 | 48 | 89 | 77 | 52 | 59 | 65 | L
Florida, Miami, New Tamiami AP | 10 | 25 | 49 | 91 | 78 | 56 | 59 | 65 | L
Florida, Milton, Whiting Field NAS | 200 | 30 | 31 | 93 | 77 | 46 | 53 | 59 | M
Florida, Ocala | 90 | 29 | 34 | 93 | 77 | 46 | 53 | 59 | M
Florida, Orlando AP | 100 | 28 | 42 | 93 | 76 | 39 | 46 | 52 | M
Florida, Panama City, Tyndall AFB | 18 | 30 | 37 | 89 | 79 | 66 | 73 | 79 | L
Florida, Pensacola CO | 30 | 30 | 32 | 92 | 78 | 54 | 61 | 67 | L
Florida, St. Augustine | 10 | 29 | 35 | 89 | 78 | 59 | 66 | 72 | M
Florida, St. Petersburg | 11 | 28 | 47 | 93 | 79 | 59 | 66 | 72 | M
Florida, Sanford | 55 | 28 | 38 | 93 | 76 | 39 | 46 | 52 | M
Florida, Sarasota/Bradenton | 30 | 27 | 43 | 92 | 79 | 61 | 68 | 74 | M
Florida, Tallahassee AP | 55 | 30 | 28 | 93 | 76 | 39 | 46 | 52 | M
Florida, Tampa AP | 19 | 28 | 40 | 91 | 77 | 49 | 56 | 62 | M
Florida, Valpariso, Eglin AFB | 85 | 30 | 33 | 90 | 78 | 57 | 64 | 70 | M
Florida, Vero Beach | 13 | 27 | 43 | 90 | 78 | 57 | 64 | 70 | M
Florida, West Palm Beach AP | 15 | 26 | 47 | 90 | 78 | 57 | 64 | 70 | M
Georgia, Albany, Turner | AFB | 223 | 31 | 30 | 95 | 76 | 49 | 56 | 62
Georgia, Americus | 466 | 32 | 25 | 94 | 76 | 37 | 44 | 50 | M
Georgia, Athens | 802 | 34 | 25 | 92 | 75 | 34 | 41 | 47 | M
Georgia, Atlanta AP | 1010 | 33 | 23 | 91 | 74 | 30 | 37 | 43 | M
Georgia, Augusta AP | 148 | 33 | 25 | 94 | 76 | 37 | 44 | 50 | M
Georgia, Brunswick | 20 | 31 | 34 | 91 | 79 | 62 | 69 | 75 | M
Georgia, Columbus, Fort Benning | 232 | 32 | 27 | 94 | 76 | 37 | 44 | 50 | M
Georgia, Columbus, Lawson AFB | 971 | 32 | 24 | 93 | 76 | 39 | 46 | 53 | M
Georgia, Columbus, Metro AP | 397 | 32 | 27 | 93 | 75 | 33 | 40 | 46 | M
Georgia, Dalton | 710 | 34 | 22 | 93 | 76 | 39 | 46 | 52 | M
Georgia, Dublin | 310 | 32 | 25 | 93 | 76 | 39 | 46 | 52 | M
Georgia, Gainesville | 1275 | 34 | 21 | 91 | 74 | 30 | 37 | 43 | M
Georgia, Griffin | 980 | 33 | 22 | 90 | 75 | 38 | 45 | 51 | M
Georgia, La Grange | 693 | 33 | 23 | 91 | 75 | 36 | 43 | 49 | M
Georgia, Macon AP | 354 | 32 | 27 | 94 | 75 | 31 | 38 | 44 | M
Georgia, Marietta, Dobbins AFB | 1068 | 34 | 26 | 91 | 74 | 30 | 37 | 43 | M
Georgia, Moultrie | 292 | 31 | 30 | 95 | 77 | 42 | 49 | 55 | M
Georgia, Rome AP | 637 | 34 | 21 | 94 | 74 | 25 | 32 | 38 | M
Georgia, Savannah, Travis AP | 49 | 32 | 29 | 93 | 76 | 39 | 46 | 52 | M
Georgia, Valdosta, Moody AFB | 233 | 31 | 34 | 94 | 77 | 44 | 51 | 57 | M
Georgia, Valdosta, Regional AP | 203 | 30 | 31 | 94 | 76 | 37 | 44 | 50 | M
Georgia, Waycross | 151 | 31 | 32 | 94 | 76 | 37 | 44 | 50 | M
Hawaii, Ewa, Barbers Point NAS | 34 | 21 | 61 | 90 | 72 | 19 | 26 | 32 | M
Hawaii, Hilo AP | 36 | 19 | 63 | 84 | 74 | 41 | 48 | 54 | L
Hawaii, Honolulu AP | 16 | 21 | 63 | 88 | 73 | 29 | 36 | 42 | L
Hawaii, Kahului | 56 | 20 | 61 | 88 | 74 | 35 | 42 | 48 | M
Hawaii, Kaneohe Bay MCAS | 18 | 21 | 68 | 85 | 74 | 40 | 47 | 53 | L
Hawaii, Lihue | 148 | 21 | 62 | 85 | 74 | 40 | 47 | 53 | L
Hawaii, Molokai | 449 | 21 | 61 | 87 | 73 | 30 | 37 | 43 | M
Hawaii, Wahaiwa | 900 | 21 | 59 | 85 | 72 | 28 | 35 | 41 | L
Idaho, Boise AP | 2838 | 43 | 9 | 94 | 63 | -34 | -27 | -21 | H
Idaho, Burley | 4150 | 42 | 2 | 90 | 62 | -22 | -15 | -9 | H
Idaho, Coeur D’Alene AP | 3002 | 47 | -1 | 86 | 61 | -30 | -23 | -17 | H
Idaho, Idaho Falls AP | 4741 | 43 | -6 | 89 | 60 | -39 | -32 | -26 | H
Idaho, Kamiah | 1196 | 46 | 15 | 93 | 64 | -28 | -21 | -14 | H
Idaho, Lewiston AP | 1413 | 46 | 15 | 93 | 64 | -28 | -21 | -15 | H
Idaho, Moscow | 2583 | 46 | 0 | 87 | 62 | -27 | -20 | -13 | H
Idaho, Mountain Home AFB | 2996 | 43 | 5 | 96 | 62 | -42 | -35 | -29 | H
Idaho, Mullan | 3317 | 47 | 7 | 84 | 61 | -27 | -20 | -14 | H
Idaho, Pocatello AP | 4454 | 43 | 0 | 90 | 60 | -41 | -34 | -28 | H
Idaho, Twin Falls AP | 4150 | 42 | 2 | 95 | 61 | -44 | -37 | -31 | H
Illinois, Aurora | 706 | 41 | -1 | 91 | 76 | 42 | 49 | 55 | M
Illinois, Belleville, Scott AFB | 453 | 38 | 10 | 93 | 77 | 46 | 53 | 59 | M
Illinois, Bloomington | 875 | 40 | -2 | 90 | 74 | 31 | 38 | 44 | M
Illinois, Carbondale | 411 | 37 | 7 | 93 | 77 | 46 | 53 | 59 | M
Illinois, Champaign/Urbana | 754 | 40 | 2 | 92 | 74 | 28 | 35 | 41 | M
Illinois, Chicago, Meigs Field | 593 | 41 | 3 | 89 | 73 | 27 | 34 | 40 | M
Illinois, Chicago, Midway AP | 620 | 41 | 0 | 91 | 73 | 24 | 31 | 37 | M
Illinois, Chicago, O’Hare AP | 668 | 42 | -1 | 88 | 73 | 29 | 36 | 42 | M
Illinois, Chicago CO | 647 | 41 | 2 | 91 | 74 | 30 | 37 | 43 | L
Illinois, Danville | 696 | 40 | 1 | 90 | 74 | 31 | 38 | 44 | M
Illinois, Decatur | 682 | 39 | 3 | 91 | 75 | 36 | 43 | 49 | M
Illinois, Dixon | 785 | 41 | -2 | 90 | 74 | 31 | 38 | 43 | M
Illinois, Elgin |  | 42 | -2 | 88 | 74 | 35 | 42 | 48 | M
Illinois, Freeport | 856 | 42 | -4 | 89 | 73 | 27 | 34 | 40 | M
Illinois, Galesburg | 764 | 41 | -2 | 91 | 75 | 36 | 43 | 49 | M
Illinois, Glenview, NAS | 653 | 42 | 4 | 89 | 73 | 27 | 34 | 40 | M
Illinois, Greenville | 541 | 39 | 4 | 92 | 75 | 34 | 41 | 47 | M
Illinois, Joliet | 581 | 41 | 0 | 90 | 74 | 31 | 38 | 43 | M
Illinois, Kankakee | 629 | 41 | 1 | 90 | 74 | 31 | 38 | 43 | M
Illinois, LaSalle/Peru | 654 | 41 | -2 | 91 | 75 | 36 | 43 | 49 | M
Illinois, Macomb | 705 | 40 | 0 | 92 | 76 | 41 | 48 | 54 | M
Illinois, Marseilles | 738 | 41 | 1 | 89 | 73 | 27 | 34 | 40 | M
Illinois, Moline, Davenport AP | 590 | 41 | -3 | 90 | 74 | 31 | 38 | 43 | M
Illinois, Mt. Vernon | 480 | 38 | 5 | 92 | 75 | 34 | 41 | 47 | M
Illinois, Peoria AP | 663 | 40 | -1 | 89 | 74 | 33 | 40 | 46 | M
Illinois, Quincy AP | 768 | 40 | 2 | 91 | 75 | 36 | 43 | 49 | M
Illinois, Rantoul, Chanute AFB | 737 | 40 | 1 | 91 | 74 | 30 | 37 | 42 | M
Illinois, Rockford | 741 | 42 | -4 | 88 | 73 | 29 | 36 | 41 | M
Illinois, Springfield AP | 641 | 39 | 2 | 91 | 75 | 36 | 43 | 49 | M
Illinois, Waukegan | 727 | 42 | -3 | 89 | 74 | 33 | 40 | 46 | M
Illinois, West Chicago | 758 | 41 | 0 | 88 | 74 | 35 | 42 | 48 | M
Indiana, Anderson | 919 | 40 | 6 | 92 | 75 | 34 | 41 | 47 | M
Indiana, Bedford | 728 | 38 | 5 | 92 | 75 | 34 | 41 | 47 | M
Indiana, Bloomington | 846 | 39 | 5 | 92 | 75 | 34 | 41 | 47 | M
Indiana, Columbus, Bakalar AFB | 656 | 39 | 7 | 92 | 75 | 34 | 41 | 47 | M
Indiana, Crawfordsville | 799 | 40 | 3 | 91 | 74 | 30 | 37 | 43 | M
Indiana, Evansville AP | 387 | 38 | 9 | 92 | 76 | 41 | 48 | 54 | M
Indiana, Fort Wayne AP | 815 | 41 | 2 | 88 | 73 | 29 | 36 | 42 | M
Indiana, Goshen AP | 827 | 41 | 1 | 89 | 73 | 27 | 34 | 40 | M
Indiana, Hobart | 644 | 41 | 2 | 88 | 73 | 29 | 36 | 42 | M
Indiana, Huntington | 806 | 40 | 1 | 89 | 72 | 21 | 28 | 34 | M
Indiana, Indianapolis AP (S) | 807 | 39 | 3 | 88 | 74 | 35 | 42 | 48 | M
Indiana, Jeffersonville | 474 | 38 | 10 | 93 | 74 | 27 | 34 | 40 | M
Indiana, Kokoma | 830 | 40 | 0 | 90 | 73 | 25 | 32 | 38 | M
Indiana, Layfayette | 607 | 40 | 3 | 90 | 75 | 38 | 45 | 51 | M
Indiana, LaPorte | 812 | 41 | 3 | 90 | 74 | 31 | 38 | 44 | M
Indiana, Marion | 859 | 40 | 0 | 90 | 73 | 31 | 38 | 44 | M
Indiana, Muncie | 937 | 40 | 2 | 90 | 73 | 25 | 32 | 38 | M
Indiana, Peru, Bunker Hill AFB | 737 | 40 | -1 | 88 | 73 | 29 | 36 | 42 | M
Indiana, Peru, Grsssom AFB | 810 | 40 | 4 | 89 | 75 | 39 | 46 | 52 | M
Indiana, Richmond AP | 1140 | 39 | 2 | 90 | 74 | 31 | 48 | 44 | M
Indiana, Shelbyville | 804 | 39 | 3 | 91 | 74 | 30 | 37 | 43 | M
Indiana, South Bend AP | 774 | 41 | 3 | 87 | 72 | 24 | 31 | 32 | M
Indiana, Terre Haute AP | 585 | 39 | 5 | 90 | 76 | 44 | 51 | 57 | M
Indiana, Valparaiso | 771 | 41 | 3 | 90 | 74 | 31 | 38 | 44 | M
Indiana, Vincennes | 414 | 38 | 6 | 92 | 74 | 28 | 30 | 41 | M
Iowa, Ames | 955 | 42 | -6 | 90 | 74 | 31 | 38 | 44 | M
Iowa, Burlington AP | 692 | 40 | 1 | 91 | 76 | 42 | 49 | 55 | M
Iowa, Cedar Rapids AP | 863 | 41 | -5 | 89 | 74 | 33 | 40 | 46 | M
Iowa, Clinton | 708 | 41 | -3 | 90 | 75 | 38 | 45 | 51 | M
Iowa, Council Bluffs | 1253 | 41 | -3 | 91 | 75 | 36 | 43 | 49 | M
Iowa, Des Moines AP | 938 | 41 | -4 | 90 | 74 | 31 | 38 | 44 | M
Iowa, Debuque | 1056 | 42 | -7 | 88 | 73 | 29 | 36 | 42 | M
Iowa, Fort Dodge | 1162 | 42 | -7 | 88 | 73 | 29 | 36 | 42 | M
Iowa, Iowa City | 661 | 41 | -6 | 89 | 76 | 46 | 53 | 59 | M
Iowa, Keokuk | 671 | 40 | 0 | 92 | 75 | 34 | 41 | 47 | M
Iowa, Lamoni | 1122 | 40 | 0 | 92 | 74 | 28 | 35 | 45 | M
Iowa, Marshalltown | 974 | 42 | -7 | 90 | 75 | 38 | 45 | 51 | M
Iowa, Mason City AP | 1213 | 43 | -10 | 88 | 73 | 29 | 36 | 42 | M
Iowa, Newton | 953 | 41 | -5 | 91 | 74 | 30 | 37 | 43 | M
Iowa, Ottumwa AP | 846 | 41 | 0 | 92 | 75 | 34 | 41 | 47 | M
Iowa, Sioux City AP | 1095 | 42 | -6 | 90 | 74 | 31 | 38 | 44 | M
Iowa, Spencer | 1339 | 43 | -11 | 88 | 73 | 29 | 36 | 41 | M
Iowa, Waterloo | 868 | 42 | -9 | 88 | 73 | 29 | 36 | 41 | M
Kansas, Atchison | 1073 | 39 | 2 | 93 | 76 | 39 | 46 | 52 | M
Kansas, Chante AP | 981 | 34 | 7 | 97 | 74 | 20 | 27 | 33 | M
Kansas, Concordia | 1483 | 39 | 3 | 96 | 72 | 10 | 17 | 23 | M
Kansas, Dodge City AP | 2582 | 37 | 6 | 97 | 70 | -3 | 4 | 10 | M
Kansas, El Dorado | 1378 | 37 | 7 | 98 | 73 | 12 | 19 | 25 | M
Kansas, Emporia | 1206 | 38 | 5 | 97 | 74 | 20 | 27 | 33 | M
Kansas, Garden City AP | 2890 | 38 | 4 | 97 | 69 | -9 | -2 | 4 | H
Kansas, Goodland AP | 3654 | 39 | 2 | 94 | 66 | -17 | -10 | -4 | H
Kansas, Great Bend | 1887 | 38 | 4 | 98 | 73 | 12 | 19 | 25 | H
Kansas, Hutchinson AP | 1542 | 38 | 8 | 99 | 72 | 5 | 12 | 18 | H
Kansas, Liberal | 2883 | 37 | 7 | 96 | 68 | -12 | -5 | 1 | H
Kansas, Manhattan, Fort Riley | 1065 | 39 | 5 | 96 | 74 | 22 | 29 | 35 | M
Kansas, Parsons | 899 | 37 | 9 | 97 | 74 | 20 | 27 | 33 | M
Kansas, Russel AP | 1864 | 38 | 3 | 96 | 72 | 10 | 17 | 23 | H
Kansas, Salina | 1272 | 38 | 4 | 97 | 73 | 14 | 21 | 27 | H
Kansas, Topeka AP | 877 | 39 | 4 | 93 | 75 | 33 | 40 | 46 | M
Kansas, Wichita AP | 1321 | 37 | 8 | 97 | 73 | 14 | 21 | 27 | M
Kansas, Wichita, McConnell AFB | 1371 | 37 | 10 | 97 | 73 | 14 | 21 | 27 | M
Kentucky, Ashland | 546 | 38 | 10 | 91 | 74 | 30 | 37 | 43 | M
Kentucky, Bowling Green AP | 547 | 37 | 14 | 91 | 75 | 36 | 43 | 49 | M
Kentucky, Corbin AP | 1188 | 37 | 9 | 92 | 73 | 23 | 29 | 36 | M
Kentucky, Covington AP | 869 | 39 | 7 | 89 | 73 | 27 | 34 | 40 | M
Kentucky, Fort Knox, Godman AAF | 753 | 37 | 15 | 92 | 74 | 28 | 35 | 41 | M
Kentucky, Hopkinsville, Campbell AFB | 571 | 15 | 15 | 93 | 76 | 39 | 46 | 52 | M
Kentucky, Jackson | 1381 | 37 | 14 | 87 | 73 | 30 | 37 | 43 | M
Kentucky, Lexington AP | 966 | 38 | 10 | 89 | 73 | 27 | 34 | 40 | M
Kentucky, Louisville AP | 477 | 38 | 12 | 90 | 75 | 38 | 45 | 51 | M
Kentucky, Madisonville | 439 | 37 | 10 | 93 | 75 | 33 | 40 | 46 | M
Kentucky, Owensboro | 407 | 37 | 10 | 94 | 75 | 31 | 38 | 44 | M
Kentucky, Paducah AP | 413 | 37 | 12 | 93 | 76 | 39 | 46 | 52 | M
Louisiana, Alexandria AP | 89 | 31 | 30 | 94 | 78 | 51 | 58 | 64 | M
Louisiana, Baton Rouge AP | 64 | 30 | 30 | 92 | 77 | 47 | 54 | 60 | M
Louisiana, Bogalusa | 119 | 30 | 28 | 93 | 77 | 46 | 53 | 59 | M
Louisiana, Bossier City, Barksdale AFB | 167 | 32 | 27 | 94 | 77 | 44 | 51 | 57 | M
Louisiana, Houma | 9 | 29 | 35 | 93 | 78 | 52 | 59 | 65 | L
Louisiana, Lafayette AP | 42 | 30 | 32 | 93 | 78 | 52 | 59 | 65 | M
Louisiana, Lake Charles AP | 9 | 30 | 32 | 91 | 78 | 56 | 63 | 69 | M
Louisiana, Leesville, Fort Polk | 330 | 31 | 30 | 94 | 76 | 37 | 44 | 50 | M
Louisiana, Minden | 278 | 32 | 25 | 96 | 76 | 34 | 41 | 47 | M
Louisiana, Monroe AP | 79 | 32 | 27 | 94 | 78 | 51 | 58 | 64 | M
Louisiana, Natchitoches | 121 | 31 | 26 | 95 | 77 | 42 | 49 | 55 | M
Louisiana, New Orleans AP | 4 | 30 | 34 | 92 | 78 | 54 | 61 | 67 | M
Louisiana, New Orleans, Lakefront AP | 10 | 30 | 39 | 92 | 78 | 54 | 61 | 67 | L
Louisiana, Shreveport AP | 254 | 32 | 26 | 95 | 77 | 42 | 49 | 55 | M
Maine, Augusta AP | 353 | 44 | 1 | 84 | 69 | 12 | 19 | 25 | M
Maine, Bangor, Dow AFB | 192 | 44 | -2 | 84 | 69 | 12 | 19 | 25 | M
Maine, Brunswick, NAS | 75 | 43 | 2 | 84 | 69 | 12 | 19 | 25 | M
Maine, Caribou AP | 624 | 46 | -10 | 82 | 67 | 5 | 12 | 18 | M
Maine, Lewiston | 358 | 44 | -2 | 85 | 70 | 15 | 22 | 29 | M
Maine, Limestone, Loring AFB | 745 | 46 | -9 | 80 | 66 | 3 | 10 | 16 | M
Maine, Millinocket AP | 413 | 45 | -9 | 83 | 68 | 8 | 15 | 21 | M
Maine, Portland | 43 | 43 | 2 | 83 | 70 | 19 | 26 | 32 | M
Maine, Waterville | 333 | 44 | -4 | 84 | 69 | 12 | 19 | 25 | M
Maryland, Balitimore AP | 148 | 39 | 15 | 91 | 74 | 30 | 37 | 43 | M
Maryland, Balitimore CO | 24 | 39 | 17 | 89 | 76 | 46 | 53 | 59 | M
Maryland, Cumberland | 790 | 39 | 10 | 89 | 74 | 33 | 40 | 46 | M
Maryland, Fredrick AP | 313 | 39 | 12 | 91 | 75 | 36 | 43 | 49 | M
Maryland, Hagerstown | 704 | 39 | 12 | 91 | 74 | 30 | 37 | 43 | M
Maryland, Lex Park, Patuxent River NAS | 39 | 38 | 21 | 90 | 75 | 38 | 45 | 51 | M
Maryland, Salisbury | 52 | 38 | 18 | 90 | 76 | 44 | 50 | 56 | M
Massachusetts, Boston AP | 20 | 42 | 12 | 87 | 71 | 19 | 26 | 32 | M
Massachusetts, Clinton | 366 | 42 | 2 | 87 | 71 | 18 | 24 | 31 | M
Massachusetts, East Falmouth, Otis ANGB | 132 | 41 | 14 | 82 | 72 | 32 | 39 | 45 | M
Massachusetts, Fall River | 190 | 41 | 9 | 84 | 71 | 23 | 30 | 36 | M
Massachusetts, Framingham | 197 | 42 | 6 | 86 | 71 | 22 | 29 | 35 | M
Massachusetts, Gloucester | 11 | 42 | 5 | 86 | 71 | 19 | 25 | 32 | L
Massachusetts, Greenfield | 250 | 42 | -2 | 85 | 71 | 21 | 27 | 34 | M
Massachusetts, Lawrence | 148 | 42 | 0 | 87 | 72 | 24 | 31 | 37 | M
Massachusetts, Lowell | 102 | 42 | 1 | 88 | 72 | 21 | 28 | 34 | M
Massachusetts, New Bedford | 80 | 41 | 9 | 82 | 71 | 27 | 34 | 40 | M
Massachusetts, Pittsfield AP | 1194 | 42 | -3 | 84 | 70 | 18 | 25 | 31 | M
Massachusetts, Springfield, Westover AFB | 195 | 42 | 0 | 87 | 71 | 19 | 26 | 32 | M
Massachusetts, Tauton | 43 | 41 | 9 | 86 | 72 | 26 | 33 | 39 | M
Massachusetts, Weymouth, S. Weymouth Nas | 161 | 42 | 11 | 87 | 72 | 24 | 31 | 37 | M
Massachusetts, Worcester AP | 986 | 42 | 5 | 83 | 69 | 14 | 21 | 27 | M
Michigan, Adrian 798 | 41 | 3 | 88 | 72 | 23 | 30 | 36 | M
Michigan, Alpena AP | 689 | 45 | -1 | 84 | 69 | 12 | 19 | 25 | H
Michigan, Battle Creek AP | 941 | 42 | 5 | 88 | 72 | 23 | 30 | 36 | M
Michigan, Benton Harbor AP | 643 | 42 | 5 | 88 | 72 | 23 | 30 | 36 | M
Michigan, Detroit | 619 | 42 | 5 | 87 | 72 | 24 | 31 | 37 | M
Michigan, Escanaba | 609 | 45 | -7 | 83 | 69 | 14 | 21 | 27 | M
Michigan, Flint AP | 771 | 42 | 3 | 86 | 71 | 20 | 27 | 33 | M
Michigan, Grand Rapids AP | 784 | 42 | 5 | 86 | 71 | 20 | 27 | 33 | M
Michigan, Hancock | 1091 | 47 | -4 | 83 | 69 | 14 | 21 | 27 | M
Michigan, Harbour Beach | 600 | 44 | 12 | 86 | 69 | 9 | 16 | 22 | M
Michigan, Holland | 603 | 42 | 6 | 86 | 71 | 20 | 27 | 33 | M
Michigan, Jackson AP | 1001 | 42 | 4 | 86 | 73 | 32 | 39 | 45 | M
Michigan, Kalamazoo | 874 | 42 | 5 | 88 | 72 | 23 | 30 | 36 | M
Michigan, Lansing AP | 841 | 42 | 2 | 86 | 72 | 26 | 33 | 39 | M
Michigan, Marquette CO | 1424 | 46 | -8 | 82 | 67 | 5 | 12 | 18 | M
Michigan, Marquette, Sawyer AFB | 1220 | 46 | -6 | 83 | 69 | 14 | 21 | 27 | M
Michigan, Mount Clemens ANGB | 583 | 42 | 7 | 87 | 72 | 24 | 31 | 37 | M
Michigan, Mt. Pleasant | 755 | 43 | 4 | 87 | 72 | 24 | 31 | 37 | M
Michigan, Muskegon AP | 625 | 43 | 7 | 83 | 70 | 19 | 26 | 32 | H
Michigan, Oscoda, Wurtsmith AFB | 634 | 44 | 3 | 86 | 71 | 20 | 27 | 33 | M
Michigan, Pellston | 719 | 45 | -3 | 86 | 69 | 9 | 16 | 22 | H
Michigan, Pontiac | 980 | 42 | 4 | 87 | 72 | 24 | 31 | 37 | M
Michigan, Port Huron | 586 | 43 | 4 | 87 | 72 | 24 | 31 | 37 | H
Michigan, Saginaw AP | 667 | 43 | 4 | 87 | 72 | 24 | 31 | 37 | M
Michigan, Sault Ste. Marie AP | 721 | 46 | -7 | 80 | 68 | 13 | 20 | 26 | M
Michigan, Seul Choix Point | 591 | 45 | 4 | 76 | 65 | 4 | 11 | 17 | M
Michigan, Traverse City AP | 624 | 44 | 2 | 86 | 70 | 14 | 21 | 27 | M
Michigan, Yipsilanti | 716 | 42 | 5 | 89 | 71 | 15 | 22 | 28 | M
Minnesota, Albert Lea | 1259 | 43 | -12 | 87 | 72 | 24 | 31 | 37 | M
Minnesota, Alexandria AP | 1424 | 45 | -15 | 86 | 70 | 14 | 21 | 27 | M
Minnesota, Bemidji AP | 1389 | 47 | -26 | 85 | 69 | 11 | 18 | 24 | M
Minnesota, Brainerd | 1280 | 46 | -17 | 85 | 68 | 5 | 12 | 18 | M
Minnesota, Duluth AP | 1428 | 46 | -16 | 81 | 67 | 6 | 13 | 19 | M
Minnesota, Fairbault | 1060 | 44 | -12 | 88 | 72 | 23 | 30 | 36 | M
Minnesota, Fergus Falls | 1182 | 46 | -17 | 88 | 72 | 23 | 30 | 36 | M
Minnesota, Hibbing | 1352 | 47 | -20 | 81 | 68 | 12 | 19 | 25 | M
Minnesota, International Falls AP | 1179 | 48 | -23 | 83 | 67 | 3 | 10 | 16 | M
Minnesota, Mankato 1020 | 44 | -12 | 88 | 72 | 23 | 30 | 36 | M
Minnesota, Minneapolis/St. Paul AP | 834 | 44 | -11 | 88 | 71 | 17 | 24 | 30 | M
Minnesota, Redwood Falls | 1024 | 44 | -12 | 88 | 72 | 23 | 30 | 36 | M
Minnesota, Rochester AP | 1297 | 44 | -12 | 85 | 71 | 22 | 29 | 35 | M
Minnesota, St. Cloud AP | 1024 | 45 | -14 | 88 | 71 | 17 | 24 | 30 | M
Minnesota, Tofte | 791 | 47 | -6 | 75 | 62 | -9 | -2 | 4 | M
Minnesota, Virginia | 909 | 47 | -21 | 83 | 68 | 8 | 15 | 22 | M
Minnesota, Willmar | 1127 | 45 | -11 | 88 | 72 | 23 | 30 | 36 | M
Minnesota, Winona | 656 | 44 | -10 | 88 | 73 | 29 | 36 | 42 | M
Mississippi, Biloxi, Keesler AFB | 26 | 30 | 35 | 91 | 78 | 56 | 63 | 69 | M
Mississippi, Clarksdale | 173 | 34 | 19 | 94 | 77 | 44 | 51 | 57 | M
Mississippi, Columbus AFB | 219 | 33 | 25 | 94 | 76 | 37 | 44 | 50 | M
Mississippi, Greenville AFB | 131 | 33 | 20 | 93 | 77 | 46 | 53 | 59 | M
Mississippi, Greenwood | 154 | 33 | 24 | 94 | 78 | 51 | 58 | 64 | M
Mississippi, Hattiesburg | 151 | 31 | 27 | 94 | 77 | 44 | 51 | 57 | M
Mississippi, Jackson AP | 310 | 32 | 25 | 93 | 76 | 36 | 46 | 52 | M
Mississippi, Laurel | 238 | 31 | 27 | 94 | 77 | 44 | 51 | 57 | M
Mississippi, McComb AP | 413 | 31 | 28 | 92 | 76 | 41 | 48 | 54 | M
Mississippi, Meridian AP | 317 | 32 | 25 | 94 | 76 | 37 | 44 | 50 | M
Mississippi, Natchez | 272 | 31 | 27 | 94 | 78 | 51 | 58 | 64 | M
Mississippi, Tupelo | 361 | 34 | 22 | 94 | 76 | 37 | 44 | 50 | M
Mississippi, Vicksburg CO | 106 | 32 | 26 | 95 | 78 | 49 | 56 | 62 | M
Missouri, Cape Girardeau | 341 | 37 | 13 | 94 | 77 | 44 | 51 | 57 | M
Missouri, Columbia AP | 778 | 39 | 5 | 92 | 75 | 34 | 41 | 47 | M
Missouri, Farmington AP | 946 | 37 | 8 | 93 | 75 | 33 | 40 | 46 | M
Missouri, Hannibal | 712 | 39 | 3 | 93 | 76 | 39 | 46 | 52 | M
Missouri, Jefferson City | 770 | 38 | 7 | 95 | 74 | 23 | 30 | 36 | M
Missouri, Joplin AP | 980 | 37 | 11 | 94 | 75 | 31 | 38 | 44 | M
Missouri, Kansas City AP | 791 | 39 | 4 | 93 | 75 | 33 | 40 | 46 | M
Missouri, Kirksville AP | 966 | 40 | 0 | 93 | 74 | 27 | 34 | 40 | M
Missouri, Mexico | 823 | 39 | 4 | 94 | 74 | 25 | 32 | 38 | M
Missouri, Moberly | 867 | 39 | 3 | 94 | 74 | 25 | 32 | 38 | M
Missouri, Poplar Bluff | 479 | 36 | 13 | 92 | 76 | 41 | 48 | 54 | M
Missouri, Rolla | 987 | 38 | 9 | 91 | 75 | 36 | 43 | 49 | M
Missouri, St. Joseph AP | 825 | 39 | 2 | 93 | 76 | 39 | 46 | 52 | M
Missouri, St. Louis AP | 535 | 38 | 8 | 93 | 75 | 33 | 40 | 46 | M
Missouri, St. Louis CO | 580 | 38 | 8 | 94 | 75 | 31 | 38 | 44 | M
Missouri, Sedalia, Whiteman AFB | 909 | 38 | 4 | 92 | 76 | 41 | 48 | 54 | M
Missouri, Sikeston | 315 | 36 | 15 | 95 | 76 | 36 | 43 | 49 | M
Missouri, Spickard/Trenton | 886 | 40 | 6 | 93 | 73 | 20 | 27 | 33 | M
Missouri, Springfield AP | 1268 | 37 | 9 | 92 | 74 | 28 | 35 | 41 | M
Missouri, Warrensburg, Whiteman AFB | 869 | 38 | 7 | 93 | 76 | 39 | 46 | 52 | M
Montana, Billings AP | 3567 | 45 | -7 | 90 | 62 | -31 | -24 | -18 | H
Montana, Bozeman | 4475 | 45 | -12 | 87 | 60 | -36 | -29 | -23 | H
Montana, Butte AP | 5553 | 46 | -14 | 84 | 56 | -51 | -44 | -38 | H
Montana, Cut Bank AP | 3838 | 48 | -16 | 84 | 59 | -36 | -29 | -23 | H
Montana, Glasgow AP | 2760 | 48 | -17 | 90 | 63 | -28 | -21 | -15 | H
Montana, Glendive | 2456 | 47 | -13 | 92 | 64 | -26 | -19 | -13 | H
Montana, Great Falls AP | 3652 | 47 | -13 | 88 | 60 | -38 | -31 | -25 | H
Montana, Great Falls, Malmstrom AFB | 3525 | 47 | -11 | 89 | 61 | -11 | -4 | 2 | H
Montana, Havre | 3200 | 48 | -19 | 90 | 62 | -33 | -26 | -20 | H
Montana, Helena AP | 3828 | 46 | -10 | 87 | 59 | -41 | -34 | -28 | H
Montana, Kalispell AP | 6780 | 48 | -3 | 86 | 61 | -29 | -22 | -16 | H
Montana, Lewiston AP | 4122 | 47 | -12 | 86 | 60 | -34 | -27 | -21 | H
Montana, Livingston AP | 4656 | 45 | -14 | 87 | 60 | -36 | -29 | -23 | H
Montana, Miles City AP | 2634 | 46 | -13 | 93 | 65 | -23 | -16 | -10 | H
Montana, Missoula AP | 3190 | 46 | -1 | 88 | 61 | -33 | -26 | -20 | H
Nebraska, Beatrice | 1323 | 40 | -2 | 95 | 74 | 28 | 35 | 41 | M
Nebraska, Bellevue, Offutt AFB | 1047 | 41 | 1 | 91 | 75 | 36 | 43 | 49 | M
Nebraska, Chadron AP | 3296 | 42 | -3 | 94 | 65 | -22 | -15 | -9 | H
Nebraska, Columbus | 1443 | 41 | -2 | 95 | 73 | 17 | 24 | 30 | M
Nebraska, Fremont | 1203 | 41 | -2 | 95 | 74 | 23 | 30 | 36 | M
Nebraska, Grand Island AP | 1841 | 41 | -2 | 93 | 72 | 15 | 22 | 28 | H
Nebraska, Hastings | 1954 | 40 | -3 | 94 | 71 | 7 | 14 | 20 | H
Nebraska, Kearney | 2131 | 40 | -4 | 93 | 70 | 3 | 10 | 16 | H
Nebraska, Lincoln CO | 1180 | 40 | -2 | 94 | 74 | 25 | 32 | 38 | M
Nebraska, McCook | 2579 | 40 | -2 | 95 | 69 | -11 | -4 | 2 | H
Nebraska, Norfolk | 1552 | 42 | -5 | 92 | 72 | 16 | 23 | 29 | H
Nebraska, North Platte AP | 2775 | 41 | -4 | 92 | 69 | -1 | 6 | 12 | H
Nebraska, Omaha AP | 977 | 41 | -2 | 92 | 75 | 34 | 41 | 47 | M
Nebraska, Omaha WSO | 1332 | 41 | -2 | 90 | 75 | 38 | 45 | 51 | M
Nebraska, Scottsbluff AP | 3958 | 41 | -3 | 92 | 64 | -25 | -18 | -12 | H
Nebraska, Sidney AP | 4304 | 41 | -1 | 92 | 63 | -29 | -22 | -16 | H
Nebraska, Valentine | 2598 | 42 | -8 | 94 | 67 | -15 | -8 | -2 | H
Nevada, Carson City | 4675 | 39 | 9 | 91 | 59 | -47 | -40 | -34 | H
Nevada, Elko AP | 5050 | 40 | 1 | 92 | 59 | -48 | -41 | -35 | H
Nevada, Ely AP | 6263 | 39 | 0 | 87 | 56 | -55 | -48 | -42 | H
Nevada, Las Vegas AP | 2162 | 36 | 30 | 106 | 66 | -39 | -32 | -26 | H
Nevada, Lovelock AP | 3904 | 40 | 12 | 96 | 63 | -35 | -28 | -22 | H
Nevada, Mercury | 3310 | 36 | 28 | 100 | 64 | -38 | -31 | -25 | H
Nevada, North Las Vega , Nellis AFB | 1868 | 36 | 31 | 106 | 67 | -34 | -27 | -21 | H
Nevada, Reno AP | 4412 | 39 | 13 | 92 | 60 | -44 | -37 | -31 | H
Nevada, Reno CO | 5046 | 39 | 11 | 93 | 60 | -45 | -38 | -32 | H
Nevada, Tonapah AP | 5426 | 38 | 13 | 92 | 57 | -58 | -51 | -45 | H
Nevada, Winnemucca AP | 4301 | 40 | 7 | 94 | 60 | -48 | -41 | -35 | H
New Hampshire, Berlin | 1161 | 44 | -9 | 84 | 69 | 12 | 19 | 25 | M
New Hampshire, Claremont | 545 | 43 | -4 | 86 | 70 | 14 | 21 | 27 | M
New Hampshire, Concord AP | 342 | 43 | -2 | 87 | 70 | 13 | 20 | 26 | H
New Hampshire, Keene | 488 | 43 | -7 | 87 | 70 | 13 | 20 | 26 | M
New Hampshire, Laconia | 545 | 43 | -5 | 86 | 70 | 14 | 21 | 27 | M
New Hampshire, Lebanon | 597 | 43 | -3 | 86 | 69 | 9 | 16 | 22 | M
New Hampshire, Manchester, Grenier AFB | 234 | 43 | -3 | 88 | 71 | 17 | 24 | 30 | M
New Hampshire, Mount Washington | 6266 | 44 | -19 | 58 | 54 | -18 | -11 | -5 | L
New Hampshire, Portsmouth, Pease AFB | 101 | 43 | 9 | 85 | 70 | 16 | 23 | 29 | M
New Jersey, Atlantic City CO | 64 | 39 | 13 | 88 | 73 | 29 | 36 | 42 | M
New Jersey, Long Branch | 36 | 40 | 13 | 90 | 73 | 24 | 30 | 37 | M
New Jersey, Millville | 82 | 39 | 15 | 89 | 74 | 33 | 40 | 46 | M
New Jersey, Newark AP | 7 | 40 | 14 | 90 | 73 | 25 | 32 | 38 | M
New Jersey, New Brunswick | 100 | 40 | 10 | 89 | 73 | 25 | 32 | 38 | M
New Jersey, Patterson | 186 | 40 | 10 | 91 | 73 | 22 | 29 | 35 | M
New Jersey, Phillipsburg | 314 | 40 | 6 | 89 | 72 | 20 | 27 | 33 | M
New Jersey, Teterboro | 9 | 40 | 14 | 89 | 74 | 33 | 40 | 46 | M
New Jersey, Trenton, McQuire AFB | 133 | 40 | 15 | 90 | 74 | 31 | 38 | 44 | M
New Jersey, Vineland | 88 | 39 | 11 | 89 | 74 | 33 | 40 | 46 | M
New Mexico, Alamagordo Holloman AFB | 4093 | 32 | 23 | 96 | 63 | -36 | -29 | -23 | H
New Mexico, Albuquerque AP | 5311 | 35 | 18 | 93 | 60 | -46 | -39 | -33 | H
New Mexico, Artesia | 3548 | 32 | 19 | 100 | 67 | -21 | -14 | -8 | H
New Mexico, Carlsbad AP | 3293 | 32 | 23 | 98 | 66 | -23 | -16 | -10 | H
New Mexico, Clayton | 4970 | 36 | 9 | 91 | 62 | -33 | -26 | -20 | H
New Mexico, Clovis, Cannon AFB | 4295 | 34 | 15 | 93 | 64 | -26 | -19 | -13 | H
New Mexico, Farmington AP | 5503 | 36 | 13 | 92 | 60 | -57 | -50 | -44 | H
New Mexico, Gallup | 6470 | 35 | 5 | 87 | 56 | -55 | -48 | -42 | H
New Mexico, Grants | 6521 | 35 | 4 | 88 | 58 | -47 | -40 | -34 | H
New Mexico, Hobbs AP | 3659 | 32 | 18 | 99 | 66 | -25 | -18 | -12 | H
New Mexico, Las Cruces | 4544 | 32 | 20 | 96 | 64 | -30 | -23 | -17 | H
New Mexico, Los Alamos | 6089 | 35 | 9 | 87 | 60 | -36 | -27 | -19 | H
New Mexico, Raton AP | 6349 | 36 | 1 | 89 | 60 | -38 | -31 | -25 | H
New Mexico, Roswell, Walker AFB | 3676 | 33 | 20 | 96 | 65 | -26 | -19 | -13 | H
New Mexico, Santa Fe CO | 6345 | 35 | 10 | 88 | 61 | -32 | -25 | -19 | H
New Mexico, Silver City AP | 6126 | 32 | 10 | 94 | 60 | -47 | -40 | -34 | H
New Mexico, Socorro AP | 4850 | 34 | 17 | 95 | 62 | -38 | -31 | -25 | H
New Mexico, Truth or Consequences | 4858 | 33 | 26 | 95 | 61 | -43 | -36 | -30 | H
New Mexico, Tucumcari AP | 4039 | 35 | 15 | 95 | 65 | -24 | -17 | -11 | H
New York, Albany AP | 285 | 42 | -2 | 86 | 70 | 14 | 21 | 27 | M
New York, Albany CO | 275 | 42 | 1 | 88 | 72 | 23 | 30 | 36 | M
New York, Auburn | 417 | 43 | 2 | 87 | 71 | 18 | 24 | 31 | M
New York, Bafavia | 913 | 43 | 5 | 87 | 71 | 19 | 26 | 32 | M
New York, Binghampton AP | 1590 | 42 | 2 | 82 | 69 | 15 | 22 | 28 | M
New York, Buffalo AP | 705 | 43 | 5 | 84 | 69 | 12 | 19 | 25 | M
New York, Central Islip | 98 | 40 | 15 | 85 | 72 | 28 | 35 | 41 | M
New York, Cortland | 1198 | 42 | 0 | 85 | 71 | 22 | 29 | 35 | M
New York, Dunkirk | 692 | 42 | 9 | 85 | 72 | 28 | 35 | 41 | M
New York, Elmira AP | 955 | 42 | 3 | 87 | 71 | 19 | 26 | 32 | M
New York, Geneva | 417 | 42 | 2 | 87 | 71 | 18 | 24 | 31 | M
New York, Glens Falls | 328 | 43 | -4 | 85 | 71 | 22 | 29 | 35 | M
New York, Gloversville | 417 | 43 | -2 | 86 | 71 | 19 | 26 | 33 | M
New York, Hornell | 1220 | 42 | 0 | 85 | 70 | 16 | 23 | 29 | M
New York, Ithaca | 1099 | 42 | 0 | 85 | 71 | 22 | 29 | 35 | M
New York, Jamestown | 1723 | 42 | 3 | 86 | 70 | 14 | 21 | 27 | M
New York, Kingston | 149 | 42 | 2 | 88 | 72 | 23 | 30 | 36 | M
New York, Lockport | 638 | 43 | 7 | 86 | 72 | 26 | 33 | 39 | M
New York, Massena AP | 213 | 44 | -10 | 84 | 71 | 23 | 30 | 36 | M
New York, Newburg-Stewart AFB | 471 | 41 | 10 | 85 | 72 | 28 | 35 | 41 | M
New York, NYC-Central Park | 7 | 40 | 15 | 89 | 73 | 27 | 34 | 40 | M
New York, NYC-Kennedy AP | 13 | 40 | 15 | 88 | 72 | 23 | 30 | 36 | M
New York, NYC-La Guardia AP | 22 | 40 | 17 | 89 | 73 | 27 | 34 | 40 | M
New York, Niagra Falls AP | 590 | 43 | 7 | 85 | 71 | 22 | 29 | 35 | M
New York, Olean | 2135 | 42 | 2 | 84 | 71 | 23 | 30 | 36 | M
New York, Oneonta | 1764 | 42 | -4 | 83 | 69 | 14 | 21 | 27 | M
New York, Oswego CO | 300 | 43 | 7 | 83 | 71 | 25 | 32 | 38 | M
New York, Plattsburg AFB | 235 | 44 | -4 | 83 | 69 | 14 | 21 | 27 | M
New York, Poughkeepsie | 165 | 41 | 6 | 88 | 72 | 23 | 30 | 36 | M
New York, Rochester AP | 547 | 43 | 5 | 86 | 71 | 20 | 27 | 33 | M
New York, Rome-Griffiss AFB | 514 | 43 | 1 | 86 | 70 | 14 | 21 | 27 | M
New York, Schenectady | 378 | 42 | 1 | 87 | 72 | 24 | 31 | 37 | M
New York, Suffolk County AFB | 67 | 40 | 10 | 83 | 71 | 25 | 32 | 38 | M
New York, Syracuse AP | 410 | 43 | 2 | 85 | 71 | 22 | 29 | 35 | M
New York, Utica | 742 | 43 | -6 | 85 | 71 | 22 | 29 | 35 | M
New York, Watertown | 325 | 44 | -6 | 83 | 7O | 19 | 26 | 32 | M
New York, White Plains | 439 | 41 | 12 | 87 | 72 | 24 | 31 | 37 | M
North Carolina, Asheville AP | 2140 | 35 | 16 | 85 | 71 | 22 | 29 | 35 | M
North Carolina, Cape Hatteras | 7 | 35 | 29 | 86 | 77 | 57 | 64 | 70 | L
North Carolina, Charlotte AP | 736 | 35 | 23 | 91 | 74 | 30 | 37 | 43 | M
North Carolina, Cherry Point MCAS | 29 | 34 | 28 | 92 | 78 | 54 | 61 | 67 | M
North Carolina, Durham | 427 | 36 | 20 | 92 | 75 | 33 | 40 | 46 | M
North Carolina, Elizabeth City AP | 12 | 36 | 19 | 91 | 77 | 49 | 56 | 62 | M
North Carolina, Fayetteville, Pope AFB | 218 | 35 | 27 | 94 | 76 | 37 | 44 | 50 | M
North Carolina, Goldsboro, Seymour | 154 | 35 | 27 | 94 | 76 | 35 | 42 | 49
North Carolina, Goldsboro, Johnson AFB | 108 | 35 | 27 | 94 | 76 | 35 | 42 | 49 | M
North Carolina, Greensboro AP | 897 | 36 | 19 | 90 | 74 | 30 | 37 | 43 | M
North Carolina, Greenville | 27 | 35 | 21 | 91 | 76 | 42 | 49 | 55 | M
North Carolina, Henderson | 2084 | 36 | 15 | 92 | 76 | 41 | 48 | 54 | M
North Carolina, Hickory | 1188 | 35 | 23 | 91 | 72 | 18 | 25 | 31 | M
North Carolina, Jacksonville | 26 | 34 | 27 | 92 | 78 | 54 | 61 | 67 | M
North Carolina, Lumberton | 126 | 34 | 21 | 92 | 76 | 41 | 48 | 54 | M
North Carolina, New Bern AP | 19 | 35 | 27 | 92 | 78 | 54 | 61 | 67 | M
North Carolina, Raleigh/Durham AP | 434 | 35 | 20 | 90 | 75 | 38 | 45 | 51 | M
North Carolina, Rocky Mount | 159 | 36 | 21 | 91 | 76 | 42 | 49 | 55 | M
North Carolina, Wilmington AP | 28 | 34 | 27 | 91 | 78 | 56 | 63 | 69 | M
North Carolina, Winston-Salem AP | 969 | 36 | 23 | 89 | 74 | 33 | 40 | 46 | M
North Dakota, Bismark AP | 1647 | 46 | -16 | 90 | 67 | -8 | -1 | 5 | H
North Dakota, Devil’s Lake | 1453 | 48 | -19 | 87 | 67 | -3 | 4 | 10 | M
North Dakota, Dickinson AP | 2585 | 46 | -17 | 90 | 66 | -13 | -6 | 0 | M
North Dakota, Fargo AP | 869 | 46 | -17 | 88 | 70 | 11 | 18 | 24 | M
North Dakota, Grands Forks AP | 911 | 48 | -16 | 88 | 69 | 6 | 13 | 19 | M
North Dakota, Jamestown AP | 1498 | 47 | -18 | 90 | 69 | 3 | 10 | 16 | H
North Dakota, Minot AP | 1668 | 48 | -16 | 88 | 66 | -10 | -3 | 3 | M
North Dakota, Minot, AFB | 1667 | 48 | -16 | 90 | 67 | -8 | -1 | 5 | H
North Dakota, Williston | 1906 | 48 | -18 | 92 | 66 | -16 | -9 | -3 | M
Ohio, Akron-Canton AP | 1228 | 41 | 5 | 85 | 71 | 22 | 29 | 35 | M
Ohio, Ashtabula | 924 | 41 | 9 | 85 | 72 | 28 | 35 | 41 | M
Ohio, Athens | 766 | 39 | 6 | 92 | 74 | 28 | 35 | 41 | M
Ohio, Bowling Green | 673 | 41 | 2 | 89 | 73 | 27 | 34 | 40 | M
Ohio, Cambridge | 800 | 40 | 7 | 90 | 74 | 31 | 38 | 44 | M
Ohio, Chilicothe | 640 | 39 | 6 | 92 | 74 | 28 | 35 | 41 | M
Ohio, Cincinnati, Lunken Field | 869 | 39 | 12 | 90 | 75 | 38 | 45 | 51 | M
Ohio, Cleveland AP | 777 | 41 | 6 | 86 | 72 | 26 | 33 | 39 | M
Ohio, Columbus AP | 812 | 40 | 6 | 88 | 73 | 29 | 36 | 42 | M
Ohio, Columbus, Rickenbckr AFB | 744 | 39 | 10 | 89 | 73 | 27 | 34 | 40 | M
Ohio, Dayton AP | 1002 | 39 | 5 | 88 | 73 | 29 | 36 | 42 | M
Ohio, Dayton, Wright/Paterson AFB | 824 | 39 | 8 | 89 | 74 | 33 | 40 | 46 | M
Ohio, Defiance | 708 | 41 | 4 | 91 | 73 | 24 | 31 | 37 | M
Ohio, Finlay AP | 810 | 41 | 4 | 87 | 72 | 24 | 31 | 37 | M
Ohio, Fremont | 663 | 41 | 1 | 88 | 73 | 29 | 36 | 42 | M
Ohio, Hamilton | 634 | 39 | 5 | 90 | 72 | 19 | 26 | 32 | M
Ohio, Lancaster | 869 | 39 | 5 | 91 | 73 | 24 | 31 | 37 | M
Ohio, Lima | 975 | 40 | 4 | 91 | 73 | 24 | 31 | 37 | M
Ohio, Mansfield AP | 1295 | 40 | 4 | 85 | 72 | 28 | 35 | 41 | M
Ohio, Marion | 994 | 40 | 5 | 91 | 73 | 24 | 31 | 37 | M
Ohio, Middletown | 651 | 39 | 5 | 90 | 72 | 19 | 26 | 32 | M
Ohio, Newark | 880 | 40 | 5 | 92 | 73 | 22 | 29 | 35 | M
Ohio, Norwalk | 852 | 41 | 1 | 88 | 73 | 29 | 36 | 42 | M
Ohio, Portsmouth | 540 | 38 | 10 | 92 | 74 | 28 | 35 | 41 | M
Ohio, Sandusky CO | 580 | 41 | 6 | 91 | 72 | 18 | 25 | 31 | M
Ohio, Springfield | 1052 | 40 | 3 | 89 | 73 | 27 | 34 | 40 | M
Ohio, Stubenville | 1194 | 40 | 5 | 86 | 71 | 20 | 27 | 33 | M
Ohio, Toledo AP | 669 | 41 | 3 | 87 | 72 | 24 | 31 | 37 | M
Ohio, Warren | 905 | 41 | 5 | 87 | 71 | 19 | 26 | 32 | M
Ohio, Wooster | 1136 | 40 | 6 | 86 | 71 | 20 | 27 | 33 | M
Ohio, Youngstown AP | 1178 | 41 | 4 | 85 | 70 | 16 | 23 | 29 | M
Ohio, Zanesville AP | 900 | 40 | 9 | 88 | 73 | 29 | 36 | 42 | M
Oklahoma, Ada | 1016 | 34 | 14 | 97 | 74 | 20 | 27 | 33 | M
Oklahoma, Altus AFB | 1378 | 34 | 19 | 100 | 73 | 9 | 16 | 22 | M
Oklahoma, Ardmore | 844 | 34 | 17 | 98 | 74 | 18 | 25 | 31 | M
Oklahoma, Bartlesville | 713 | 36 | 10 | 98 | 74 | 18 | 25 | 31 | M
Oklahoma, Chickasha | 1150 | 35 | 14 | 98 | 74 | 18 | 25 | 31 | M
Oklahoma, Enid-Vance AFB | 1307 | 36 | 12 | 98 | 74 | 18 | 25 | 31 | M
Oklahoma, Lawton AP | 1188 | 34 | 19 | 97 | 73 | 14 | 21 | 27 | M
Oklahoma, McAlester | 776 | 34 | 17 | 96 | 76 | 34 | 41 | 47 | M
Oklahoma, Muskogee AP | 610 | 35 | 15 | 98 | 75 | 25 | 32 | 38 | M
Oklahoma, Norman 1181 | 35 | 13 | 96 | 74 | 22 | 29 | 35 | M
Oklahoma, Oklahoma City AP | 1262 | 35 | 17 | 96 | 75 | 28 | 35 | 41 | M
Oklahoma, Oklahoma City, W.Rogers AP | 1285 | 35 | 15 | 96 | 74 | 22 | 29 | 35 | M
Oklahoma, Ponca City | 1007 | 36 | 9 | 97 | 74 | 20 | 27 | 33 | M
Oklahoma, Seminole | 1021 | 35 | 15 | 96 | 74 | 22 | 29 | 41 | M
Oklahoma, Stillwater | 984 | 36 | 13 | 96 | 74 | 22 | 29 | 41 | M
Oklahoma, Tulsa AP | 650 | 36 | 14 | 97 | 76 | 33 | 40 | 46 | M
Oklahoma, Woodward | 2188 | 36 | 10 | 97 | 73 | 14 | 21 | 27 | H
Oregon, Albany | 223 | 44 | 22 | 89 | 66 | -12 | -5 | 1 | H
Oregon, Astoria AP | 8 | 46 | 29 | 72 | 63 | 0 | -7 | -13 | M
Oregon, Baker AP | 3369 | 44 | 6 | 89 | 61 | -35 | -28 | -22 | H
Oregon, Bend | 3453 | 44 | 4 | 87 | 60 | -36 | -29 | -23 | H
Oregon, Corvallis | 246 | 44 | 22 | 89 | 66 | -12 | -5 | 1 | H
Oregon, Eugene AP | 359 | 44 | 26 | 87 | 65 | -14 | -7 | -1 | H
Oregon, Grants Pass | 925 | 42 | 24 | 96 | 68 | -12 | -5 | 1 | H
Oregon, Hillsboro | 203 | 45 | 24 | 88 | 67 | -5 | 2 | 8 | H
Oregon, Klamath Falls AP | 4092 | 42 | 10 | 87 | 62 | -26 | -19 | -13 | H
Oregon, Meacham | 4055 | 45 | 0 | 84 | 58 | -41 | -34 | -28 | H
Oregon, Medford AP | 1298 | 42 | 24 | 95 | 66 | -21 | -14 | -8 | H
Oregon, North Bend | 748 | 43 | 32 | 69 | 60 | -8 | -1 | 5 | M
Oregon, Pendleton AP | 1482 | 45 | 11 | 93 | 63 | -33 | -26 | -20 | H
Oregon, Portland AP | 30 | 45 | 27 | 86 | 66 | -7 | 0 | 6 | M
Oregon, Portland CO | 35 | 45 | 24 | 86 | 67 | -2 | 5 | 11 | M
Oregon, Redmond | 3084 | 44 | 9 | 89 | 61 | -35 | -28 | -22 | H
Oregon, Roseburg AP | 525 | 43 | 23 | 90 | 66 | -13 | -6 | 0 | H
Oregon, Salem AP | 196 | 45 | 25 | 87 | 66 | -8 | -1 | 5 | H
Oregon, Sexton Summit | 3842 | 42 | 24 | 80 | 59 | -30 | -23 | -17 | M
Oregon, The Dalles | 243 | 45 | 19 | 89 | 68 | -1 | 6 | 12 | H
Pennsylvania, Allentown AP | 387 | 40 | 10 | 88 | 72 | 23 | 30 | 36 | M
Pennsylvania, Altoona CO | 1504 | 40 | 10 | 86 | 70 | 14 | 21 | 27 | M
Pennsylvania, Bradford | 2142 | 41 | -1 | 80 | 68 | 13 | 20 | 26 | M
Pennsylvania, Butler | 1248 | 40 | 6 | 87 | 72 | 24 | 31 | 37 | M
Pennsylvania, Chambersburg | 697 | 40 | 8 | 90 | 74 | 31 | 38 | 44 | M
Pennsylvania, DuBois | 1818 | 41 | 5 | 84 | 69 | 12 | 19 | 25 | M
Pennsylvania, Erie AP | 731 | 42 | 7 | 83 | 70 | 19 | 26 | 32 | M
Pennsylvania, Harrisburg AP | 308 | 40 | 13 | 89 | 73 | 27 | 34 | 40 | M
Pennsylvania, Johnstown | 2284 | 40 | 2 | 83 | 70 | 19 | 26 | 32 | M
Pennsylvania, Lancaster | 403 | 40 | 8 | 90 | 74 | 31 | 38 | 44 | M
Pennsylvania, Meadville | 1400 | 41 | 4 | 85 | 70 | 16 | 23 | 29 | M
Pennsylvania, New Castle | 825 | 41 | 7 | 88 | 72 | 23 | 30 | 36 | M
Pennsylvania, Philadelphia AP | 5 | 39 | 15 | 89 | 74 | 33 | 40 | 46 | M
Pennsylvania, Philadelphia, Northeast AP | 121 | 40 | 15 | 90 | 74 | 31 | 38 | 44 | M
Pennsylvania, Philadelphia, Willow Gr NAS | 361 | 40 | 14 | 90 | 74 | 31 | 38 | 44 | M
Pennsylvania, Pittsburgh AP | 1137 | 40 | 7 | 86 | 70 | 14 | 21 | 27 | M
Pennsylvania, Pittsburgh, Allegheny AP | 1353 | 40 | 7 | 88 | 71 | 17 | 24 | 30 | M
Pennsylvania, Reading CO | 266 | 40 | 13 | 89 | 72 | 210 | 28 | 34 | M
Pennsylvania, Scranton/Wilkes-Barre | 930 | 41 | 7 | 85 | 70 | 16 | 20 | 26 | M
Pennsylvania, State College | 1239 | 40 | 7 | 87 | 71 | 19 | 26 | 32 | M
Pennsylvania, Sunbury | 430 | 40 | 7 | 89 | 72 | 21 | 28 | 34 | M
Pennsylvania, Uniontown | 815 | 39 | 9 | 88 | 73 | 29 | 36 | 42 | M
Pennsylvania, Warren | 1193 | 41 | 4 | 86 | 71 | 20 | 27 | 33 | M
Pennsylvania, West Chester | 466 | 40 | 13 | 89 | 74 | 33 | 40 | 46 | M
Pennsylvania, Williamsport AP | 524 | 41 | 7 | 87 | 71 | 19 | 26 | 32 | M
Pennsylvania, York | 480 | 40 | 12 | 91 | 74 | 30 | 37 | 43 | M
Rhode Island, Newport | 10 | 41 | 9 | 85 | 72 | 28 | 35 | 41 | M
Rhode Island, Providence AP | 51 | 41 | 10 | 86 | 71 | 20 | 27 | 33 | M
South Carolina, Anderson | 782 | 34 | 23 | 92 | 74 | 28 | 35 | 41 | M
South Carolina, Beaufort, MCAS | 38 | 32 | 31 | 93 | 78 | 52 | 59 | 65 | M
South Carolina, Charleston AFB | 45 | 32 | 28 | 92 | 77 | 47 | 54 | 60 | M
South Carolina, Charleston CO | 3 | 32 | 28 | 92 | 78 | 54 | 61 | 67 | L
South Carolina, Columbia AP | 213 | 34 | 24 | 94 | 75 | 31 | 38 | 44 | M
South Carolina, Florence AP | 147 | 34 | 27 | 94 | 76 | 37 | 44 | 50 | M
South Carolina, Georgetown | 14 | 33 | 26 | 90 | 78 | 57 | 64 | 70 | M
South Carolina, Greenville AP/Greer | 957 | 34 | 23 | 91 | 74 | 30 | 37 | 43 | M
South Carolina, Greenwood | 631 | 34 | 22 | 93 | 74 | 27 | 34 | 40 | M
South Carolina, Myrtle Beach, AFB | 25 | 33 | 29 | 90 | 78 | 57 | 64 | 70 | M
South Carolina, Orangeburg | 197 | 33 | 24 | 95 | 75 | 29 | 36 | 42 | M
South Carolina, Rock Hill | 667 | 35 | 23 | 94 | 74 | 25 | 32 | 38 | M
South Carolina, Spartanburg AP | 801 | 35 | 22 | 91 | 74 | 30 | 37 | 43 | M
South Carolina, Sumter-Shaw AFB | 252 | 34 | 29 | 93 | 75 | 33 | 40 | 46 | M
South Dakota, Aberdeen AP | 1296 | 45 | -15 | 91 | 72 | 18 | 25 | 31 | H
South Dakota, Brookings | 1647 | 44 | -13 | 92 | 72 | 16 | 23 | 29 | M
South Dakota, Chamberlain | 1739 | 43 | -7 | 94 | 71 | 7 | 14 | 20 | H
South Dakota, Huron AP | 1281 | 44 | -12 | 91 | 71 | 12 | 19 | 25 | H
South Dakota, Mitchell | 1303 | 43 | -10 | 93 | 71 | 9 | 16 | 22 | H
South Dakota, Pierre AP | 1742 | 44 | -9 | 95 | 69 | -6 | 1 | 7 | H
South Dakota, Rapid City AP | 3162 | 44 | -5 | 91 | 65 | -18 | -11 | -5 | H
South Dakota, Sioux Falls AP | 1418 | 43 | -11 | 90 | 72 | 19 | 26 | 32 | M
South Dakota, Watertown AP | 1748 | 45 | -15 | 91 | 72 | 18 | 25 | 31 | H
South Dakota, Yankton | 1305 | 43 | -7 | 91 | 72 | 28 | 35 | 41 | M
Tennessee, Athens | 858 | 33 | 18 | 92 | 73 | 22 | 29 | 35 | M
Tennessee, Bristol-Tri City AP | 1507 | 36 | 14 | 87 | 72 | 24 | 31 | 37 | M
Tennessee, Chattanooga AP | 665 | 35 | 20 | 92 | 75 | 34 | 41 | 47 | M
Tennessee, Clarksville | 550 | 36 | 12 | 93 | 74 | 27 | 34 | 40 | M
Tennessee, Columbia | 681 | 35 | 15 | 94 | 74 | 25 | 32 | 38 | M
Tennessee, Crossville | 1880 | 35 | 15 | 87 | 72 | 24 | 31 | 37 | M
Tennessee, Dyersburg | 338 | 36 | 15 | 94 | 77 | 44 | 51 | 57 | M
Tennessee, Greenville | 1608 | 35 | 16 | 90 | 72 | 19 | 26 | 32 | M
Tennessee, Jackson AP | 433 | 35 | 18 | 93 | 76 | 39 | 46 | 52 | M
Tennessee, Knoxville AP | 980 | 35 | 19 | 90 | 74 | 31 | 38 | 44 | M
Tennessee, Memphis AP | 258 | 35 | 21 | 94 | 77 | 44 | 51 | 57 | M
Tennessee, Murfreesboro | 615 | 35 | 14 | 94 | 74 | 25 | 32 | 38 | M
Tennessee, Nashville AP | 590 | 36 | 16 | 92 | 75 | 34 | 41 | 47 | M
Tennessee, Tullahoma | 1072 | 35 | 13 | 93 | 73 | 20 | 27 | 33 | M
Texas, Abilene AP | 1790 | 32 | 22 | 97 | 71 | 2 | 9 | 15 | M
Texas, Alice AP | 178 | 27 | 34 | 98 | 77 | 37 | 44 | 50 | M
Texas, Amarillo AP | 3604 | 35 | 12 | 94 | 66 | -17 | -10 | -4 | H
Texas, Austin AP | 597 | 30 | 30 | 96 | 74 | 22 | 29 | 35 | M
Texas, Bay City | 45 | 29 | 33 | 94 | 77 | 59 | 66 | 72 | M
Texas, Beaumont | 16 | 30 | 32 | 92 | 79 | 61 | 68 | 74 | M
Texas, Beeville | 190 | 28 | 33 | 98 | 77 | 37 | 44 | 50 | M
Texas, Big Springs AP | 2561 | 32 | 20 | 97 | 69 | -9 | -2 | 4 | M
Texas, Brownsville AP | 19 | 25 | 40 | 94 | 77 | 44 | 51 | 57 | H
Texas, Brownwood | 1386 | 31 | 22 | 99 | 73 | 11 | 18 | 24 | M
Texas, Bryan AP | 322 | 30 | 29 | 96 | 75 | 28 | 35 | 41 | M
Texas, Corpus Christi AP | 19 | 27 | 36 | 94 | 78 | 51 | 58 | 64 | M
Texas, Corsicana | 448 | 32 | 25 | 98 | 75 | 25 | 32 | 38 | M
Texas, Dallas, Fort Worth AP | 537 | 32 | 24 | 98 | 74 | 18 | 25 | 31 | M
Texas, Del Rio, Laughlin AFB | 1026 | 29 | 32 | 98 | 73 | 12 | 19 | 25 | M
Texas, Denton | 642 | 33 | 22 | 99 | 74 | 17 | 24 | 30 | M
Texas, Eagle Pass | 884 | 28 | 32 | 99 | 73 | 11 | 18 | 24 | M
Texas, El Paso AP | 3918 | 31 | 25 | 98 | 64 | -33 | -26 | -20 | H
Texas, Fort Worth, Carswell AFB | 650 | 32 | 22 | 99 | 74 | 17 | 24 | 30 | M
Texas, Fort Worth, Meacham Field | 709 | 32 | 24 | 98 | 74 | 18 | 25 | 31 | M
Texas, Galveston AP | 7 | 29 | 36 | 89 | 79 | 51 | 58 | 64 | L
Texas, Greenville | 535 | 33 | 22 | 99 | 74 | 17 | 24 | 30 | M
Texas, Guadalupe Pass | 5453 | 31 | 19 | 89 | 60 | -39 | -32 | -26 | M
Texas, Harlingen | 35 | 26 | 39 | 94 | 77 | 44 | 51 | 57 | M
Texas, Houston AP | 96 | 29 | 31 | 94 | 77 | 44 | 51 | 57 | M
Texas, Houston, Hobby AP | 46 | 29 | 34 | 93 | 77 | 46 | 53 | 59 | M
Texas, Huntsville | 363 | 30 | 27 | 98 | 75 | 25 | 32 | 38 | M
Texas, Junction | 1713 | 30 | 23 | 98 | 71 | 1 | 8 | 14 | H
Texas, Killeen-Gray AFB | 1014 | 31 | 27 | 96 | 73 | 16 | 23 | 29 | M
Texas, Kingsville, NAS | 50 | 27 | 36 | 96 | 78 | 47 | 54 | 60 | M
Texas, Lamesa | 2998 | 32 | 17 | 96 | 69 | -7 | 0 | 6 | H
Texas, Laredo AFB | 512 | 27 | 36 | 101 | 74 | 14 | 21 | 27 | M
Texas, Longview 365 | 32 | 24 | 97 | 76 | 33 | 40 | 46 | M
Texas, Lubbock AP | 3254 | 33 | 17 | 95 | 67 | -13 | -6 | 0 | H
Texas, Lubbock, Reese AFB | 3338 | 33 | 18 | 95 | 67 | -14 | -7 | -1 | H
Texas, Lufkin AP | 277 | 31 | 27 | 95 | 77 | 42 | 49 | 55 | M
Texas, Marfa | 4859 | 30 | 19 | 92 | 61 | -39 | -32 | -26 | H
Texas, McAllen | 108 | 26 | 40 | 98 | 76 | 31 | 38 | 44 | M
Texas, Midland AP | 2851 | 32 | 22 | 97 | 67 | -19 | -12 | -6 | H
Texas, Mineral Wells AP | 972 | 32 | 22 | 99 | 74 | 17 | 24 | 30 | M
Texas, Palestine CO | 422 | 31 | 27 | 98 | 76 | 31 | 38 | 44 | M
Texas, Pampa | 3244 | 35 | 12 | 96 | 67 | -15 | -8 | -2 | H
Texas, Pecos | 2611 | 31 | 21 | 98 | 69 | -10 | -3 | 3 | H
Texas, Plainview | 3374 | 34 | 13 | 96 | 68 | -10 | -3 | 3 | H
Texas, Port Arthur AP | 16 | 30 | 31 | 93 | 78 | 52 | 59 | 65 | M
Texas, San Angelo, Goodfellow AFB | 1877 | 31 | 24 | 97 | 70 | -3 | 4 | 10 | M
Texas, San Antonio AP | 788 | 29 | 30 | 96 | 73 | 16 | 23 | 29 | M
Texas, San Antonio, Kelly AFB | 690 | 29 | 32 | 97 | 74 | 20 | 27 | 33 | M
Texas, San Antonio, Randolph AFB | 761 | 29 | 31 | 96 | 74 | 22 | 29 | 35 | M
Texas, Sanderson | 2838 | 30 | 28 | 95 | 68 | -11 | -4 | 2 | M
Texas, Sherman-Perrin AFB | 763 | 33 | 20 | 98 | 75 | 25 | 32 | 38 | M
Texas, Snyder | 2430 | 32 | 18 | 98 | 70 | -5 | 2 | 8 | M
Texas, Temple | 682 | 31 | 27 | 99 | 74 | 17 | 24 | 30 | M
Texas, Tyler AP | 544 | 32 | 24 | 97 | 76 | 33 | 40 | 46 | M
Texas, Vernon | 1264 | 34 | 17 | 100 | 73 | 9 | 16 | 22 | M
Texas, Victoria AP | 115 | 28 | 33 | 94 | 76 | 37 | 44 | 50 | M
Texas, Waco AP | 501 | 31 | 26 | 99 | 75 | 23 | 30 | 36 | M
Texas, Wichita Falls AP | 994 | 34 | 19 | 100 | 73 | 9 | 16 | 22 | M
Utah, Cedar City AP | 5626 | 37 | 8 | 91 | 59 | -47 | -40 | -34 | H
Utah, Logan | 4454 | 41 | 2 | 91 | 61 | -37 | -30 | -24 | H
Utah, Moab | 4553 | 38 | 11 | 98 | 60 | -53 | -46 | -40 | H
Utah, Ogden, Hill AFB | 4785 | 41 | 11 | 90 | 60 | -41 | -34 | -28 | H
Utah, Price | 5921 | 39 | 5 | 91 | 60 | -42 | -35 | -29 | H
Utah, Provo | 4448 | 40 | 6 | 96 | 62 | -40 | -33 | -27 | H
Utah, Richfield | 5279 | 38 | 5 | 91 | 60 | -42 | -35 | -29 | H
Utah, St. George CO | 2941 | 37 | 21 | 101 | 65 | -36 | -29 | -23 | H
Utah, Salt Lake City AP | 4220 | 40 | 11 | 94 | 62 | -37 | -30 | -24 | H
Utah, Vernal AP | 5274 | 40 | 0 | 89 | 60 | -39 | -32 | -26 | H
Vermont, Barre | 1165 | 44 | -11 | 81 | 69 | 17 | 24 | 30 | M
Vermont, Burlington AP | 332 | 44 | -6 | 84 | 69 | 12 | 19 | 25 | M
Vermont, Montpelier/ Barre | 1165 | 44 | -6 | 83 | 68 | 8 | 15 | 21 | M
Vermont, Rutland | 787 | 43 | -8 | 84 | 70 | 18 | 25 | 31 | M
Virginia, Charlottsville | 870 | 38 | 18 | 91 | 74 | 30 | 37 | 43 | M
Virginia, Danville AP | 572 | 36 | 16 | 92 | 73 | 22 | 29 | 35 | M
Virginia, Fort Belvoir | 69 | 38 | 18 | 93 | 76 | 39 | 46 | 52 | M
Virginia, Fredricksburg | 85 | 38 | 14 | 93 | 75 | 33 | 40 | 46 | M
Virginia, Hampton, Langley AFB | 10 | 37 | 24 | 91 | 77 | 49 | 56 | 62 | M
Virginia, Harrisonburg | 1201 | 38 | 16 | 91 | 72 | 18 | 25 | 31 | M
Virginia, Lynchburg AP | 916 | 37 | 17 | 90 | 74 | 31 | 38 | 44 | M
Virginia, Newport News | 41 | 37 | 22 | 92 | 77 | 47 | 54 | 60 | M
Virginia, Norfolk AP | 22 | 36 | 24 | 91 | 76 | 42 | 49 | 55 | M
Virginia, Oceana, NAS | 22 | 36 | 25 | 91 | 76 | 42 | 49 | 55 | M
Virginia, Petersburg | 193 | 37 | 17 | 92 | 76 | 41 | 48 | 54 | M
Virginia, Quantico MCAS | 12 | 38 | 21 | 92 | 76 | 41 | 48 | 54 | M
Virginia, Richmond AP | 164 | 37 | 18 | 92 | 75 | 34 | 41 | 47 | M
Virginia, Roanoke AP | 1193 | 37 | 17 | 89 | 72 | 21 | 28 | 34 | M
Virginia, Staunton | 1201 | 38 | 16 | 91 | 72 | 18 | 25 | 31 | M
Virginia, Sterling | 322 | 38 | 14 | 90 | 74 | 31 | 38 | 44 | M
Virginia, Reagan, National AP | 66 | 38 | 20 | 92 | 76 | 41 | 48 | 54 | M
Virginia, Winchester | 727 | 39 | 10 | 90 | 74 | 31 | 38 | 44 | M
Washington, Aberdeen | 12 | 47 | 28 | 77 | 62 | -12 | -5 | 1 | M
Washington, Bellingham AP | 158 | 48 | 21 | 76 | 64 | -1 | 6 | 12 | M
Washington, Bremerton | 7 | 47 | 25 | 78 | 64 | -4 | 3 | 9 | M
Washington, Ellensburg AP | 1760 | 47 | 6 | 91 | 64 | -25 | -18 | -12 | H
Washington, Everett-Paine AFB | 596 | 47 | 25 | 76 | 64 | -1 | 6 | 12 | M
Washington, Hanford | 732 | 46 | 12 | 96 | 65 | -28 | -21 | -15 | H
Washington, Kennewick | 531 | 46 | 11 | 96 | 67 | -18 | -11 | -5 | H
Washington, Longview | 12 | 46 | 24 | 85 | 67 | 0 | 7 | 13 | H
Washington, Moses Lake, Larson AFB | 1185 | 47 | 7 | 94 | 65 | -25 | -18 | -12 | H
Washington, Olympia AP | 215 | 47 | 23 | 83 | 65 | -7 | 0 | 6 | H
Washington, Port Angeles | 288 | 48 | 27 | 69 | 61 | -4 | 3 | 9 | M
Washington, Quillayute | 201 | 47 | 27 | 74 | 61 | -12 | -5 | 1 | M
Washington, Seattle-Boeing Fld | 18 | 47 | 28 | 81 | 64 | -9 | -2 | 4 | M
Washington, Seattle CO | 14 | 47 | 27 | 82 | 66 | 0 | 7 | 13 | M
Washington, Seattle-Tacoma AP | 429 | 47 | 26 | 80 | 64 | -7 | 0 | 6 | M
Washington, Spokane AP | 2366 | 47 | 7 | 89 | 61 | -36 | -29 | -23 | M
Washington, Stampede Pass | 3967 | 47 | 10 | 74 | 56 |  |  |  | M
Washington, Tacoma-McChord AFB | 322 | 47 | 24 | 82 | 63 | -15 | -8 | -2 | M
Washington, Walla Walla AP | 1206 | 46 | 12 | 95 | 65 | -26 | -19 | -13 | H
Washington, Wenatchee | 1243 | 47 | 9 | 92 | 65 | -21 | -14 | -8 | H
Washington, Yakima AP | 1052 | 46 | 11 | 92 | 64 | -26 | -19 | -13 | H
West Virginia, Beckley | 2504 | 37 | 4 | 81 | 69 | 17 | 24 | 30 | M
West Virginia, Bluefield AP | 2858 | 37 | 12 | 83 | 69 | 14 | 21 | 27 | M
West Virginia, Charleston AP | 939 | 38 | 11 | 88 | 73 | 29 | 36 | 42 | M
West Virginia, Clarksburg | 1203 | 39 | 10 | 90 | 73 | 25 | 32 | 38 | M
West Virginia, Elkins AP | 1948 | 38 | 5 | 83 | 70 | 19 | 26 | 32 | M
West Virginia, Huntington CO | 828 | 38 | 11 | 89 | 73 | 27 | 34 | 40 | M
West Virginia, Martinsburg AP | 556 | 39 | 14 | 91 | 73 | 24 | 33 | 39 | M
West Virginia, Morgantown AP | 1247 | 39 | 11 | 87 | 71 | 19 | 26 | 32 | H
West Virginia, Parkersburg CO | 858 | 39 | 11 | 88 | 72 | 23 | 32 | 38 | M
West Virginia, Wheeling | 1195 | 40 | 5 | 86 | 71 | 20 | 27 | 33 | M
Wisconsin, Appleton | 918 | 44 | -9 | 86 | 72 | 26 | 33 | 39 | M
Wisconsin, Ashland | 826 | 46 | -16 | 82 | 68 | 10 | 17 | 23 | M
Wisconsin, Beloit | 817 | 42 | -3 | 90 | 75 | 38 | 45 | 51 | M
Wisconsin, Eau Claire AP | 907 | 44 | -13 | 87 | 71 | 19 | 26 | 32 | M
Wisconsin, Fond du Lac | 809 | 43 | -8 | 86 | 72 | 26 | 33 | 39 | M
Wisconsin, Green Bay AP | 682 | 44 | -8 | 85 | 72 | 28 | 35 | 41 | M
Wisconsin, LaCrosse AP | 651 | 43 | -8 | 88 | 73 | 29 | 36 | 42 | M
Wisconsin, Madison AP | 858 | 43 | -6 | 87 | 72 | 24 | 31 | 37 | M
Wisconsin, Manitowoc | 651 | 44 | -7 | 86 | 72 | 26 | 33 | 39 | M
Wisconsin, Marinette | 703 | 45 | -11 | 84 | 71 | 23 | 30 | 36 | M
Wisconsin, Milwaukee AP | 723 | 43 | -2 | 86 | 72 | 26 | 33 | 39 | M
Wisconsin, Racine | 674 | 42 | -2 | 88 | 73 | 29 | 36 | 42 | M
Wisconsin, Sheboygan | 749 | 43 | -6 | 86 | 73 | 32 | 39 | 45 | M
Wisconsin, Stevens Point | 1110 | 43 | -11 | 89 | 73 | 27 | 34 | 40 | M
Wisconsin, Waukesha | 911 | 43 | -5 | 87 | 73 | 33 | 40 | 46 | M
Wisconsin, Wausau AP | 1201 | 44 | -9 | 85 | 70 | 16 | 23 | 29 | M
Wyoming, Big Piney | 6990 | 42 | -15 | 80 | 53 | -58 | -51 | -45 | H
Wyoming, Casper AP | 5348 | 42 | -5 | 89 | 58 | -49 | -42 | -36 | H
Wyoming, Cheyene AP | 6156 | 41 | 0 | 85 | 57 | -47 | -40 | -34 | H
Wyoming, Cody AP | 5098 | 44 | -7 | 87 | 58 | -45 | -38 | -32 | H
Wyoming, Evanston | 7163 | 41 | -3 | 84 | 55 | -55 | -48 | -42 | H
Wyoming, Gillette | 4363 | 44 | -7 | 91 | 61 | -38 | -31 | -25 | H
Wyoming, Lander AP | 5586 | 42 | -7 | 87 | 58 | -46 | -39 | -33 | H
Wyoming, Laramie AP | 7278 | 41 | -6 | 81 | 56 | -46 | -39 | -33 | H
Wyoming, Newcastle | 4174 | 43 | -12 | 87 | 63 | -21 | -14 | -8 | H
Wyoming, Rawlins | 6813 | 41 | -4 | 83 | 57 | -44 | -37 | -31 | H
Wyoming, Rock Springs AP | 6760 | 41 | -2 | 84 | 54 | -60 | -53 | -47 | H
Wyoming, Sheridan AP | 4024 | 44 | -8 | 90 | 61 | -36 | -29 | -23 | H
Wyoming, Torrington | 4205 | 42 | -8 | 91 | 62 | -32 | -25 | -19 | H
Wyoming, Worland | 4227 | 43 | -13 | 93 | 63 | -30 | -23 | -17 | H

## Wrk D (hidden)
Worksheet D HTM Values and Net Area for Opaque Panels | [15 empty] | CLTD Adjustments
[16 empty] | Summer design CTD = |  | 13
Month |  |  | Hour | Latitude | HTD | Midsummer 3 pm |  | Month / Hour |  | Daily | OD = Outdoor ID = Indoor DB = Dry Bulb (°F) |  | Type of space load |  |  |  | Mid Summer OD Design = | 88 |  |  | Month 3 pm OD Dsn = | 88
[6 empty] | OD DB | ID DB | OD DB | ID DB | Range |  |  | Room #; Zone # or Block |  |  |  | Mid Summer ID Dsn = | 75 |  |  | Month/Hr OD Dsn = | 88
Jul & Aug |  |  | 15:00 | 34 | 26 | 88 | 75 | 88 | 75 | 20 |  |  | Zone |  |  | Color adjustment: Dark = 1.20; Light = 0.78 |  |  |  |  | Month/Hr ID Dsn = | 75
Const. No. and Expose Direction; or Ceiling Slope |  |  | Width | Average | Gross | Opening | Net | Slab | U-Value | HTD | Group | Adjust'd | Heating | Cooling |  | CLTD Adjustment for Doors and Walls
|  |  | or | Height | Area | Area | Area | Edge | or Slab | or | Number | CLTD | HTM | HTM |  | Doors & | Base | Mo / Lat | Color | Dsn Temp | Daily | Adjust'd CLTD
|  |  | Length | or Width | (SqFt) | (SqFt) | (SqFt) | (Ft) | F-Value | PTDH | T-4A | T-4B |  |  |  | Walls | CLTD | DB Adjust | Adjust | Adjust | Range | CLTD
| Direction > |  | (Ft) | (Ft) |  |  |  |  | T-4A |  |  | or PTDC |  |  |  |  | T-4A | Tbl 1F | DF = 1.0 | (F) | Adjust
Wood and Metal Doors (Construction 11) | [8 empty] | HTD = | 26 | [5 empty] | Adjusted CLTD for Doors (see Table 4A, Construction 11)
a | 0 | 0 | 1 | 0 | 0 | Use gross area if < 50 %; use French door if > 50%. |  |  |  | 26 |  | 26 | 0 | 0 | 0 | a | 26 |  | 1 | 0 |  | 26 | 11 | 0
b | 0 | 0 | 1 | 0 | 0 |  |  |  |  | 26 |  | 26 | 0 | 0 | 0 | b | 26 |  | 1 |  |  | 26 | 12 | -7
c | 0 | 0 | 1 | 0 | 0 |  |  |  |  | 26 |  | #N/A | 0 | 0 | 0 | c | 26 |  | #N/A |  |  | #N/A | 13 | -7
Above Grade Walls (Construction 12, 13 and 14) | [8 empty] | HTD = | 26 | [5 empty] | Adjusted CLTD for Walls (see Table 4B, CLTD Adjustment for Exposed Walls) | [6 empty] | 14 | -7
a | 13CB-0fc Block, Framing w/ R-13 cavity, drywall | West | 200 | 1 | 200 |  | 200 |  | 0.073 | 26 | I | 18 | 1.898 | 1.314 | 1.314 | a | 25 |  | 1 | -7 | 0 | 18 | 16 | 0
b | 0 | 0 | 0 | 1 | 0 |  | 0 |  |  | 26 |  | #N/A |  |  |  | b | #N/A |  | 1 |  |  | #N/A | 17 | -7
c | 0 | 0 | 0 | 1 | 0 |  | 0 |  |  | 26 |  | #N/A |  |  |  | c | #N/A |  | 1 |  |  | #N/A | 19 | 0
d | 0 | 0 | 0 | 1 | 0 |  | 0 |  |  | 26 |  | #N/A |  |  |  | d | #N/A |  | 1 |  |  | #N/A | 18 | 0
e | 0 | 0 | 0 | 1 | 0 |  | 0 |  |  | 26 |  | #N/A |  |  |  | e | #N/A |  | #N/A |  |  | #N/A | 20 | 0
f | 0 | 0 | 0 | 1 | 0 |  | 0 |  |  | 26 |  | #N/A |  |  |  | f | #N/A |  | #N/A |  |  | #N/A
g | 0 | 0 | 0 | 1 | 0 |  | 0 |  |  | 26 |  | #N/A |  |  |  | g | #N/A |  | #N/A |  |  | #N/A
h | 0 | 0 | 0 | 1 | 0 |  | 0 |  |  | 26 |  | #N/A |  |  |  | h | #N/A |  | #N/A |  |  | #N/A
p1 | 13CB-0fc Block, Framing w/ R-13 cavity, drywall | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073 | 0 | 0 | 0 | 0 | 0 | 0
p2 | 12B-0s-m Frame wall, Metal studs, R-11 cavity, wood sheathing, siding | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.122 | 0 | 0 | 0 | 0 | 0 | 0
Partition Walls (Construction 12, 13 and 14) — Use estimated partition temperature difference for heating (PTDH) and cooling (PTDC)
p1 | 13CB-0fc Block, Framing w/ R-13 cavity, drywall |  |  |  | 516 |  | 516 |  | 0.073 | 0 |  | 0 | 0 | 0 | ← | PTDH and TPDC from heat balance calc, or see Table 4C
p2 | 12B-0s-m Frame wall, Metal studs, R-11 cavity, wood sheathing, siding |  |  |  | 396 |  | 396 |  | 0.122 |  |  |  | 0 | 0
Below Grade Walls (Construction 15) | [8 empty] | HTD = | 26
a |  |  |  |  | 0 | [7 empty] | 0
b |  |  |  |  | 0 | [7 empty] | 0
c |  |  |  |  | 0 | [7 empty] | 0
Ceilings and Roofs (Construction 16, 16-ecap, 17A, 17B, 17C, 17D and 18)
Form N1 has three lines for ceilings. |  |  |  |  | Use lines 42 to 55 to evaluate CLTD values for ceilings | [10 empty] | Adjusted | Base | Mo / Lat | Color | Dsn Temp | Daily | Adjust'd CLTD
Const. No. and Expose Direction; or Ceiling Slope |  |  | Average | Average | Gross | Opening | Net | RA Ceiling | Roof or | HTD or | Group | Adjust'd | Heating | Cooling |  | Ceiling | CLTD | Adjust | Adjust | Adjust | Range | CLTD
|  |  | Room | Room | Area Adjst | Area | Area | Under | Ceiling | PTDH | Number | CLTD | HTM | HTM |  | CLTD | T-4A | Tbl 1F | DF = 1.0 | (F) | Adjust
|  |  | Length | Width | for Slope | (SqFt) | (SqFt) | Roof or | U-value | Blank for | Tbl 4A | Tbl 4B |  |  |  | Const. 16 Ceilings (see Table 4B, 24 Hour CLTDs for Construction 16)
|  |  | (Ft) | (Ft) | (SqFt) |  |  | Floor | Table 4A | RA Ceiling |  | or PTDC |  |  |  | Const. 17 A and B Ceilings (see Tbl 4B CLTD Adjust. for Const. 17 )
Ceiling Slope > |  | Θ | [6 empty] | HTD = | 26 | [5 empty] | Const. 17C & 17D (ceiling under RA cavity) = Wrks D1 or D2
a | 17A-15m Metal deck plus R-15 board, no ceiling |  | 1117 | 1 | 1117 |  | 1117 | na | 0.061 | 26 | R13 | 18.74 | 1.586 | 1.1431 | 1.1431 | 18.74 | 33 |  | 0.78 | -7 | 0 | 18.74 | -7
b | 0 |  | 0 | 1 | 0 |  | 0 |  |  | 26 |  |  | 0 | 0 | 0 | #VALUE! |  |  |  | #N/A | 0 | #VALUE! | #N/A
c | 0 |  | 0 | 1 | 0 |  | 0 |  |  | 26 |  |  | 0 | 0 | 0 | #VALUE! |  |  |  | #N/A | 0 | #VALUE! | #N/A
Floors (Construction 17D, 19, 20, 21 and 22) | [8 empty] | Note: Use F-value and running feet of exposed edge for slab floors
Form N1 has three lines for floors. |  |  |  |  | Use lines 61 to 71 to evaluate CLTD values for ceilings
Const. Number |  |  | Average | Average | Gross | For Slab | Slab | Floor Area | U-Value | HTD | Group | Adjust'd | Heating | Cooling |  | Adjusted | Base | Mo / Lat | Color | Dsn Temp | Daily | Adjust'd CLTD
|  |  | Length | Width | Area | Enter 1 | Edge | or Edge Ft | or Slab | or | Number | CLTD | HTM | HTM |  | Floor | CLTD | Adjust | Adjust | Adjust | Range | CLTD
|  |  | (Ft) | (Ft) | (SqFt) | or Leave | (Ft) | for | F-Value | PTDH | Tbl 4A | Tbl 4B |  |  |  | CLTD | T-4A | Tbl 1F | DF = 1.0 | (F) | Adjust
[6 empty] | Blank |  | Form N1 | Tbl 4A |  |  | or PTDC |  |  |  | Const. 20A Floors (see Tbl 4A CLTD Adjust. for Const. 18 )
[6 empty] | Blank or 1 | Blank or Ft |  | HTD = | 26 | [5 empty] | Const. 20B Floors (see Tbl 4B CLTD Adjust. for Const. 20B )
a | 0 |  | 1 | 0 | 0 |  |  | 0 |  |  |  | #VALUE! | 0 | 0 | 0 | #VALUE! |  |  |  | 0 |  | #VALUE! | 0
b | 0 |  | 1 | 0 | 0 |  |  | 0 |  |  |  | #VALUE! | 0 | 0 | 0 | #VALUE! |  |  |  | 0 |  | #VALUE! | 0
c | 0 |  | 1 | 0 | 0 |  |  | 0 |  | 26 |  | #VALUE! | 0 | 0 | 0 | #VALUE! |  |  |  | 0 |  | #VALUE! | 0
d | 0 |  | 1 | 0 | 0 |  |  | 0 |  | 26 |  | #VALUE! | 0 | 0 | 0 | #VALUE! |  |  |  | 0 |  | #VALUE! | 0
e | 0 |  | 1 | 0 | 0 |  |  | 0 |  | 26 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  | 0
f | 22B-10pm Slab on grade, 2" Edge Insulation, Heavy Dry or Light Wet Soil |  | 1 |  |  |  | 116 | 116 | 0.355 | 26 |  | 0 | 9.23 | 0 | 0 | 0 | 0 |  |  | 0 |  | 0
[5 empty] | 1117 | [10 empty] | Adjusted CLTD (PTDC) for #19 floors (see Tbl 4A, Construction 19 )
General Notes: | [15 empty] | Adjusted CLTD (PTDC) for #17D floors (over RA cavity) = Wrks D2
1) Heating HTM = U x HTD or U x PTDH; Cooling HTM = U x Adjusted CLTD or U x PTDC | [15 empty] | Adjusted CLTD for #21 (basement) floors = 0
2) CLTD adjustment depends on construction number. | [15 empty] | Adjusted CLTD for #22 (slab) floors = 0
3) Export heating and cooling HTM values and net (or gross) areas to Form N1. | Key Saver Worksheet (Floor Areas and Above Grade Volumes for Worksheet F)
Mandatory Input for Automated Infiltration Calculation!
| A) Ceiling Load, No Floor Load |  |  |  | Average Above |  | Heating | Cooling | AGV | AGV | AGV | Floor Area | Floor Area | Area
| True = 1 | Use procedure D ceiling area |  |  | Grade Wall |  | True = 1 | True = 1 | Heating | Cooling | Total | Heating | Cooling | for Horz
| or blank | for floor area of cond space |  |  | Height (Ft) |  | or blank | or blank | (CuFt) | (CuFt) | (CuFt) | (SqFt) | (SqFt) | Plane
| 1 | a | 1117 |  | 9 |  | 1 | 1 | 10053 | 10053 | 10053 | 1117 | 1117 | 1117
|  | b | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  | c | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B) Floor Load For Whole Floor |  |  |  | Average Above |  | Heating | Cooling | AGV | AGV | AGV | Floor Area | Floor Area | Floor Area
| True = 1 | Use procedure D floor area |  |  | Grade Wall |  | True = 1 | True = 1 | Heating | Cooling | Total | Heating | Cooling | Total
| or blank | for floor area of cond space |  |  | Height (Ft) |  | or blank | or blank | (CuFt) | (CuFt) | (CuFt) | (SqFt) | (SqFt) | (SqFt)
|  | a | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  | b | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  | c | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| C) User input for Floor Load |  |  |  | Average Above |  | Heated | Cooled | AGV | AGV | AGV | Floor Area | Floor Area | Floor Area
| True = 1 | Name of conditioned space |  |  | Grade Wall |  | Floor Area | Floor Area | Heating | Cooling | Total | Heating | Cooling | Total
| or blank |  |  |  | Height (Ft) |  | (SqFt) | (SqFt) | (CuFt) | (CuFt) | (CuFt) | (SqFt) | (SqFt) | (SqFt)
|  | a | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  | b | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  | c | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0
| For ACH values, use entire floor area for both floors and the second floor volume! | [6 empty] | Totals | 10053 | 10053 |  | 1117 | 1117
[8 empty] | KBW Input | 13404 | 13404
Note on N41: PTDC for RA ceiling from Wrk D1 or D2
Note on E68: If a Procedure D ceiling or ceiling partition covers the entire space (level) below the ceiling and if this space has no floor load, no floor-partition load, a partial exposed floor load or a partial floor-partition load enter 1 in column B. If there is an exposed floor load or floor-partition load for the entire level below the ceiling, leave the cell blank.
Note on G68: Average above grade wall height for the space of consideration. (For an irregular shape, divide the panel area by the panel length.)
Note on I68: Enter 1 if space below ceiling is heated.
Note on J68: Enter 1 if space below ceiling has cooling.
Note on C69: Enter a 1 for the cases that apply.
Note on E74: If a Procedure D floor load or floor-partition load applies to the entire space (level) above the floor, enter 1 in column B. If a Procedure D floor load or floor-partition load only applies to part of the level above the floor, leave the cell blank.
Note on G74: Average above grade wall height for the space of consideration. (For an irregular shape, divide the panel area by the panel length.)
Note on I74: Enter 1 if space below ceiling is heated.
Note on J74: Enter 1 if space below ceiling has cooling.
Note on C75: Enter a 1 for the cases that apply.
Note on E80: If a conditioned space has no ceiling or floor load, a partial exposed ceiling load, a partial exposed floor load, a partial ceiling-partition load or a partial floor-partition load, enter 1 in column B and type a name for the space in column C. If the space has an exposed ceiling load, an exposed floor load, a ceiling-partition or a floor-partition load that applies to the entire space, use Case A or Case B.
Note on G80: Average above grade wall height for the space of consideration. (For an irregular shape, divide the panel area by the panel length.)
Note on I80: Enter heated floor area of space.
Note on J80: Enter cooled floor area of space.
Note on C81: Enter a 1 for the cases that apply.

## Welcome
Welcome to the electronic spreadsheet version for the ACCA
abridged version (ae) of Manual N, 5th Edition (N5) -- Commercial Load Calculations, 2008
A thorough understanding of N5 Part 1 (Basic Manual N Procedures) as well as a working knowledge of Microsoft
Excel are prerequisites for using this spreadsheet.
To minimize data entry, this spreadsheet uses revised versions of the printed N5ae worksheets.
The tab labeled Database must be populated with building component information that is commonly
used in your construction market. This information will then be used as various lookup tables in the
GlassI, SkylightI, DoorI, WallI, CeilingI and FloorI tabs. Use the printed N5 book as the
information source for the required values.
Use the printed N5 manual for guidance to enter information into the InternalI, DuctsI, InfiltrationI
and VentilationI tabs.
You can now populate the header portion of the N1 Form and the six Input Tabs to create default
templates to minimize data selection for future Manual N load calculations.
Microsoft Excel version 97 is the minimum requirement to use the spreadsheet but Microsoft
Excel version 2000 or greater is recommended to utilize the full features of the spreadsheet.
We strongly suggest that you print out and read the instructions on using this electronic spreadsheet
that are contained in the following Help tab.
This spreadsheet can be downloaded from the ACCA System Design website. |  | ACCA System Design
Please visit the website often to check for updates to the spreadsheet. The most recent version
number is listed on Notes tab.

## Help
ACCA Manual N, 5th Edition, Abridged Version
*** Refer to the Notes Tab to verify the latest revision ***
Help Section
Refer to Manual N Load Calculations for Low-Rise Commercial Buildings, Fifth Edition Version 1.xx
Step 1: Go to the Form N1 tab and select your default design state and city .
Step 2: Go to the Database tab and enter the building components used most frequently in your geographic and market area.
The items entered here can be selected later from a custom list of your component inputs reducing the time to sort
thru hundreds of possible choices that may never be used in your area. The database can have items added or
changed as the need arises. Note: Database entries must correspond to the design conditions selected in step 1.
Important: The Construction Number must always be included and precede the description for the Database entries
Glass Database
Enter construction numbers 1 thru 7 and 10 from tables 2A & 2C
Enter a description that corresponds to the construction number
Enter the frame construction that corresponds to the construction number
Enter the U-Value that corresponds to the construction number and frame type
Enter the SHGC that corresponds to the construction number and frame type
Skylights Database
Enter construction numbers 8 and 9 from table 2A
Enter a description that corresponds to the construction number
Enter the frame construction that corresponds to the construction number
Enter the Ueff that corresponds to the construction number and frame type
Enter the SHGC that corresponds to the construction number and frame type
Doors Database
Enter construction number 11 from table 4A
Enter a description that corresponds to the construction number
Enter the U-Value that corresponds to the construction number
Walls Database
Enter construction numbers 12 thru 15 from table 4A
Enter a description that corresponds to the construction number
Enter the U-Value that corresponds to the construction number
Enter the Group Code that corresponds to the construction number
Ceilings Database
Enter construction numbers 16 thru 18 from table 4A
Enter a description that corresponds to the construction number
Enter the U-Value that corresponds to the construction number
Enter the Group Code that corresponds to the construction number
Floors Database
Enter construction numbers 19 thru 22 from table 4A
Enter a description that corresponds to the construction number
Enter the U-Value or F-Value that corresponds to the construction number
Enter the PTDH if applicable that corresponds to the construction number
Enter the PTDC, CLTD or Group Code if applicable that corresponds to the construction number
Notes:
Construction numbers 19 thru 21 uses U-Value
Construction number 22 uses F-Value
Construction number 19 uses PTDC
Construction number 20A uses CLTD
Construction number 20B uses Group Code
Step 3: Save the spreadsheet now with a unique name(s) that will be used as your template to start a new load
calculation. (Example: MN5 Nashville TN 05NOV07.xls) You can create as many templates as needed
for possible different design conditions or construction methods.
Step 4: Now you are ready to start a new load calculation. Open the saved template from Step 3 and fill out the header portion
of the Form N1 tab.
Note: All Yellow cells are for data entry, Blue cells contain formulas, and Green cells contain descriptive text.
Enter the Project Name, Square Feet and Above Grade Volume of conditioned space
The default indoor design conditions are pre-set but may be changed
Select the Design Hour of Day
Step 5: From the Form N1 you can select the Lookup hyperlink to go to the component input screen to select and enter your
construction types and values. From the input screens you can select the Return to Form N1 hyperlink to go back to
the Form N1.
Glass Input: Enter the type of glass, quantity, direction, dimensions, internal shading, adjustments and overhang adjustments
Skylight Input: Enter the type of skylight, direction, net square feet and tilt angle
Door Input: Enter the type of door direction, net square feet and color
Wall Input: Enter the type of wall, direction, net square feet and color
|  |  | ● | Partition Wall Input: Enter the type of wall, net square feet, PTDH and PTDC
Ceiling Input: Enter the type of ceiling, net square feet and color
Floor Input: Enter the type of floor and square feet.
|  |  | ● | Slab Floor Input: Enter the type of floor and linear feet
Internal Input:
Lights: Enter the quantity, watts and diversity factor
Occupants: Enter the quantity, activity level and diversity factor
Office Equipment: Enter the quantity, name plate watts or BTUH, any latent values and diversity factor
Plants: Enter the quantity and size
Blower Heat: Select blow thru or draw thru and if additional return fan if applicable
Ducts Input: Enter the type of duct system, insulation, leakage class, installed square feet of surface area or default of 1 and
estimated heating and cooling ambient temperatures for specific duct location
Infiltration Input: Enter the levels of exposure and tightness
Ventilation Input: Enter the type of ventilation and corresponding value
|  |  | ● | Return to the Form N1 to verify your entries and results. If acceptable proceed to Step 6
Step 6: Select File and Save As and replace the current file name with a unique file name for this load calculation.
(Example: John Smith New Residence) You may want to create a file folder on the hard drive to store your load
|  |  | calculations in the event to need to re-call the load calculation for review or revisions. |  |  |  | (Example: MN5 Loads)
Step 7: Print the Form N1

## Read Me (hidden)
Comparison of Manual N Procedures
Version | N4 | N5ae | N5
Standard and Code Compliance
ANSI/ASHRAE/ACCA Standard 183 Note 1 | No | No | Yes
Existing Local Code | Possibly, see local code | Not for code adoption | Adoption by Reference
Existing Utility Regulation | Possibly, see local regulation | Not for regulatory use | Adoption by Reference
HVAC Licensing test | Possibly, see local requirement | ACCA offers assistance to testing authorities; contact Glenn Hourhan
Practitioner Implementation
Learning Curve (prerequisite) | Entry level (Manual J experience helpful) | Entry level (MJ8ae useful; MJ8 preferred) | Advanced (MJ8 and N5ae preferred)
Implementation by Hand Calculations | Yes (but time consuming) | Yes (computer spreadsheet recommended) | Possible (not recommended; use computer)
Type of Building
Residential Structure CCU | No | Yes (uses MJ8 construction database)
True Commercial Structure | Yes | Yes (uses improved version of N4 construction database)
General Exclusions | Buildings that have an atrium, glass roof, glass barrel vault, indoor swimming pool, indoor fountain or reflection pool, active solar system or passive solar features; any space used as a solarium; any space that has a hot tub, steam room or sauna.
Height of Building | Three stories or less (infiltration procedures do not evaluate high-rise stack effect for thermal envelope and elevator shafts).
Foot Print Area | No limit, providing the capabilities and sensitivities of the procedure are compatible with the attributes of the application.
Zoning and Zoning Issues Note 2 | Yes (no guidance or discussion) | Yes (discussion and some guidance) | Yes (discussion and more guidance)
Below Grade Walls and Floors | Yes (minimal and out dated) | No | Yes (current and extensive)
Ceiling Cavity Used for Return Air plenum | Yes (approximate defaults) | No | Yes (heat balance procedure)
HVAC Equipment and Systems
Limit on Equipment Size | No limit, providing the capabilities and sensitivities of the procedure are compatible with the attributes of the application.
Single Zone Equipment | Yes | Yes | Yes
Multizone Equipment Note 2 | Yes (no guidance or examples) | No (example for multiple 1-zone units) | Yes (examples for multizone equipment)
All Air Systems | Yes (no procedure for fan heat) | Yes (includes fan heat) | Yes (includes fan heat)
Hot Water or Steam System | No procedure for piping load | No procedure for piping load | Yes
Chilled Water System | No procedure for piping and pump load | No procedure for piping and pump load | Yes
Radiant Pipe or Elements in Floor | No | Yes | Yes
Make-Up Air and Exhaust Note 3 | No guidance (procedure is capable) | No | Protocol and guidance provided
Heat Recovery Equipment | No | No | Yes
Winter Humidification Equipment | Yes | No | Yes
Evaluation of Part Load Performance | No | No | Yes Note 4
Climate
Month of Year | Midsummer | Midsummer | 12 Months
Time of Day | 9 am; Noon; 3 pm and 6 pm | 9 am; Noon; 3 pm and 6 pm | 24 Hours
Locations | USA and Canada 2-1/2% and 97-1/2% | USA and Canada | USA; Canada; MC for AR, CA, HI and NV
Altitude Adjustment | No | Yes | Yes
Protocol for design temperature value | 2-1/2% and 97-1/2% (superseded) | 1.0% and 99.0% (current) | 0.4, 1.0, 2.0 %; 99.6, 98.0, 99.0 %
Glass
NFRC Rated and Labeled | No | Yes | Yes
Generic | 1/4 Inch | 1/8 and 1/4 Inch | 1/8 and 1/4 Inch
Solar Affect (including OH shade line) | Midsummer; 9 am; Noon; 3 pm and 6 pm | Midsummer; 9 am; Noon; 3 pm and 6 pm | 12 Months and 24 Hours
Vertical Glass Adjustments | OH, IS, SS | OH, IS, PA, S, SS | OH, IS, PA, IS, SS, FR
Skylight Adjustments | Tilt angle | Tilt angle, curb options, LS options, IS | Tilt angle, curb options, LS options, IS
Opaque Surfaces
Roof Only or Roof Over Dead Air Cavity | Yes | Yes | Yes
Roof Over Return Air Plenum | Yes (approximate defaults) | No | Yes (heat balance procedure)
Ceiling Under an Attic | Yes (no sensitivity to important issues) | Yes (sensitivity to roof material and color; and adjustment for use of radiant barrier)
Ceiling Under a Return Air Plenum | Plenum under a roof | No | Plenum under a roof or a conditioned space
Above Grade Walls | Traditional commercial | Improved traditional commercial and the entire MJ8 data base
Floors | Slab | Over CCS, exposed, slab | Over CCS, exposed, basement, slab
Partitions | Inadequate guidance for TD | TD from heat balance procedure (general) or table for garage wall or ceiling
Infiltration
Tightness Categories | Tight, Average, Poor, Loose | Tight, Medium-Tight, Average, Medium-Loose, Loose
Protocol for Choosing Tightness Category | No | Yes
Adjustment for Space Pressure | Yes (crude defaults) | No (neutral pressure only) | Yes (use equation for actual air balance)
Guidance for acceptable space pressure | Yes | Not applicable | Yes (improved)
Door Traffic (man and overhead doors) | Yes (limited options and TR guidance) | Yes (more door and TR options, and improved TR guidance)
Option to Use Blower Door test | No | No | Yes
Internal Gain
CLF Procedure to Convert Gain to Load | No | No | Yes
Lights | Incandescent and basic fluorescent | Most types of lamps and ballasts in current use
Space and cavity load for RA light fixture | Inadequate and obsolete defaults | No | Load fractions for four types of fixtures
Occupancy | Yes (obsolete) | Yes (updated activities and Btuh values, animals and plants added)
Modern Office Equipment (computers, etc.) | No | Yes | Yes
Motors and Motor Driven Equipment | Inadequate guidance | No guidance | Comprehensive guidance
Kitchen and Food Service Equipment | Yes (obsolete) | No guidance | Updated and improved data base
Gains that Require Investigation Note 5 | No guidance | No guidance | Summary of requirements and protocol
Hot pipes, hot Surfaces and Steam Release | No guidance | No guidance | Yes
Cold Pipes and Cold Display Cases | No guidance | No guidance | Yes
Evaporation from Wet Surface | No guidance | No guidance | Yes
Gains or Losses for Hygroscopic Material | No guidance | No guidance | Yes
Ducts
Validity | Superseded by N5 Procedures | N5 and MJ8 use the same model, which conforms to ASHRAE Standard 153
Type of Load | Sensible heating and sensible cooling | Sensible heating, sensible cooling and latent cooling
Locations | Four loosely defined locations | Attic, ceiling or floor cavity, below slab | Ten locations with differentiating attributes
Ambient Temperature and Humidity | No information | Protocol and equations for explicit dry-bulb temperature and ΔGrains moisture values
Use of Return Air Plenum | Yes | No | Yes
Leakage Categories | No allowance for leakage | Five categories from very tight to Standard 153 default for unsealed
Duct Insulation R-Values | None, R2, R4 and R6 | R2, R4, R6 and R8 (R0 requires use of computer model, or default to R2)
Routing Geometry | No information | Radial/Spider or Orthogonal trunk and branch
Airway Shape | No information | Round or Rectangular
Floor Area of Conditioned Space | No information | 3,000; 6,000; 9,000; 12,000 and 15,000 SqFt
System Airflow Rate (ALF) | No information | ALF (Cfm per SqFt floor area) = 0.50, 1.0, 1.5, 2.0, 2.5, 3.0, 3.5, 4.0. 4.5, 5.0
Default Values for Duct Surface Area | No Information | Default values for supply-side and return side conform to Manual Q procedures
Actual Values for Duct Surface Area | Not supported | Use values from field measurements or from plans
Duct in More than One Type of Space | Footnote: Use weighted average | No | Worksheet procedure
Return Air Load for Return Air Plenum | 40% of ceiling lights and roof load | No | Heat balance calculation, actual conditions
Engineered Ventilation
Outdoor Air Cfm for Health and Safety | Superseded by N5 Procedures | Discussion of issues and resources, practitioner shall conform to codes and standards
Outdoor Air Cfm for Load Calculation | Void health and safety Cfm from 1970's | Table provides defaults for various applications
Space has Exhaust Hood or Equipment | Supported | Not supported | Supported
Consider Makeup Air and Damper Leakage | Compare outdoor air Cfm for occupants with make-up air Cfm requirement and damper leakage Cfm, then use largest value
Adjustment for Heat Recovery Equipment | No | No | Adjustment for sensible and latent recovery
Evaluate Ventilation Dehumidifier | No | No | Yes
Ancillary Loads and System Loads
Winter Humidification Load | Yes, minimal guidance | No | Yes, comprehensive guidance
Hot Water and Steam Distribution | No | No | Yes
Chilled Water Distribution | No | No | Yes
Blower Heat | No | Blow-through or draw-through supply fan, return air fan
Chilled Water Pump | No | No | Yes
Latent Moisture Migration Load | No | No | Yes
Forms and Worksheets
Form N1 -- Load Summary | Use one N1 Form per space (for room zone or block load)
Worksheets | None (minimal guidance on Form N1) | Comprehensive procedures for every item on Form N1
Acronyms
CCU = Converted to Commercial Use; MC = Micro Climate; OH = Overhang; IS = Internal Shade; PA = Projected Assembly; S = Screen (insect); SS = Sun Screen; FR = Foreground Reflectance LS = Light Shaft; CCS = Closed Crawl Space; TD = Temperature Difference; TR = Traffic Rate; CLF = Cooling Load Factor; ALF = Air Loading Factor
Notes
1) Standard 183 specifies requirements for load calculation procedures for buildings except low-rise residential buildings.
2) Any procedure that can do one room can do any number of zones. The practitioner shall properly group and evaluate spaces for the peak load month and hour of day.
3) Exhaust and make-up air equipment affect space pressure, infiltration load and ventilation load.
4) Load vs. outdoor temperature graphs show yearly load patterns, heating-cooling change-over and minimum cooling load for space and for equipment.
5) Applies to most types of medical, laboratory, electronic, food service, cleaning-washing and process equipment (impossible to provide defaults for everything that may be encountered).

## Form N1
Manual N, 5th Edition, Abridged Version · Form N1
|  | Project Name | Maria's Rest. Zone 1 |  |  | Heating Design 99% DB | 44 | Heating Design Space DB |  | 70 | Heating Temp. Difference |  | 26
|  | Design State | California |  |  | Cooling Design 1% DB | 88 | Cooling Design Space DB |  | 75 | Cooling Temp. Difference |  | 13
|  | Design City | Long Beach Daughtery Field |  |  | Coincident Wet Bulb | 67 | Rel Hum Design Space % |  | 50 | Design Grains Difference |  | 3
|  | Type of Load | Zone |  |  | Elevation | 39 | Latitude |  | 34 | Daily Range |  | M
|  | Square Feet | 1117 | AG Volume | 13404 | Altitude Correction Factor | 1 | Design Month |  | Jul & Aug | Design Hour of Day |  | 15:00
Type of Exposure |  | Construction Number & Description |  |  |  |  | Panel Faces | HTM |  | Net Area or Length | Btuh
[8 empty] | Heating | Cooling |  | Heating | Clg Sensible | Clg Latent
► Lookup | a | 1c-cuf-c Double pane, fixed sash, Metal no break |  |  |  |  | East | 17.94 | 54.855 | 160 | 2870.4 | 8776.8
Windows & Glass Doors | b | 1c-cuf-c Double pane, fixed sash, Metal no break |  |  |  |  | East | 17.94 | 54.855 | 20.25 | 363.285 | 1110.8138
| c | 0 |  |  |  |  | 0 |  |  | 0
| d | 0 |  |  |  |  | 0 |  |  | 0
| e | 0 |  |  |  |  | 0 |  |  | 0
| f | 0 |  |  |  |  | 0 |  |  | 0
| g | 0 |  |  |  |  | 0 |  |  | 0
| h | 0 |  |  |  |  | 0 |  |  | 0
► Lookup | a | 0 |  |  |  |  | 0 |  |  | 0
Skylights | b | 0 |  |  |  |  | 0 |  |  | 0
| c | 0 |  |  |  |  | 0 |  |  | 0
| d | 0 |  |  |  |  | 0 |  |  | 0
| e | 0 |  |  |  |  | 0 |  |  | 0
► Lookup | a | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
Wood & Metal Doors | b | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| c | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
► Lookup | a | 13CB-0fc Block, Framing w/ R-13 cavity, drywall |  |  |  |  | West | 1.898 | 1.314 | 200 | 379.6 | 262.8
Above Grade Walls | b | 0 |  |  |  |  | 0 |  |  | 0
| c | 0 |  |  |  |  | 0 |  |  | 0
| d | 0 |  |  |  |  | 0 |  |  | 0
| e | 0 |  |  |  |  | 0 |  |  | 0
| f | 0 |  |  |  |  | 0 |  |  | 0
| g | 0 |  |  |  |  | 0 |  |  | 0
| h | 0 |  |  |  |  | 0 |  |  | 0
Partition Walls | p1 | 13CB-0fc Block, Framing w/ R-13 cavity, drywall |  |  |  |  | 0 | 0 | 0 | 516 | 0 | 0
| p2 | 12B-0s-m Frame wall, Metal studs, R-11 cavity, wood sheathing, siding | [5 empty] | 0 | 0 | 396 | 0 | 0
► Lookup | a | 17A-15m Metal deck plus R-15 board, no ceiling | [5 empty] | 1.586 | 1.1431 | 1117 | 1771.562 | 1276.8874
Ceilings | b | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
| c | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
► Lookup | a | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
Floors | b | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
| c | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
| d | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
| e | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
| f | 22B-10pm Slab on grade, 2" Edge Insulation, Heavy Dry or Light Wet Soil | [5 empty] | 9.23 | 0 | 116 | 1070.68 | 0
► Lookup | a | Lighting Fixtures | [9 empty] | 3430.065
Internal | b | Occupants & Plants | [9 empty] | 17001 | 16029
| c | Office Equipment | [9 empty] | 285.25 | 0
| d | Food Service Equipment and Investigated Loads | [9 empty] | 6076 | 3745
| e | Blower Heat (Building Load) | [9 empty] | 0 | 0
► Lookup |  | Infiltration | [5 empty] | 1.287 | 0.66124 |  | 8222.7288 | 2112.4246 | 301.3529
► Lookup |  | Supply Duct Load | [5 empty] | 0 | 0 |  | 0 | 0
|  | Return Duct Load | [5 empty] | 0 | 0 |  | 0 | 0 | 0
► Lookup |  | Ventilation Loads | [6 empty] | CFM | 689 | 19705.4 | 9852.7 | 1405.56
► Lookup |  | Blower Heat (Equipment Load) | [9 empty] | 0
[8 empty] | Total Loads |  |  | 34383.6558 | 50184.7407 | 21480.9129

## Database
Glass Data (Table 2A & 2C, Construction Numbers 1-7,10) | [7 empty] | PSF
Const. Code | Description | Frame Construction |  | U-Value | SHGC |  |  | North |  | NE/NW | E/W | SE/SW | South
1c-cuf-c | Double pane, fixed sash | Metal no break | 1c-cuf-c Double pane, fixed sash, Metal no break | 0.69 | 0.63 |  |  | 140.75 |  | 260.75 | 218.5 | 140.75 | 184.75
1c-cuf-c | Double pane, fixed sash | Metal with break | 1c-cuf-c Double pane, fixed sash, Metal with break | 0.63 | 0.63 |  |  | 140.75 |  | 260.75 | 218.5 | 140.75 | 184.75
1c-cuf-c | Double pane, fixed sash | Wood or wood clad | 1c-cuf-c Double pane, fixed sash, Wood or wood clad | 0.56 | 0.61 |  |  | 140.75 |  | 260.75 | 218.5 | 140.75 | 184.75
1c-cuf-c | Double pane, fixed sash | Insulated fiberglass | 1c-cuf-c Double pane, fixed sash, Insulated fiberglass | 0.56 | 0.61 |  |  | 140.75 |  | 260.75 | 218.5 | 140.75 | 184.75
1A-cuf-c | Single pane 1/4" glass, fixed sash | Metal no break | 1A-cuf-c Single pane 1/4" glass, fixed sash, Metal no break | 1.13 | 0.74 |  |  | 140.75 |  | 260.75 | 218.5 | 140.75 | 184.75
1A-cuo-c | Single pane 1/4" glass, operable glass | Metal no break | 1A-cuo-c Single pane 1/4" glass, operable glass, Metal no break | 1.27 | 0.71 |  |  | 140.75 |  | 260.75 | 218.5 | 140.75 | 184.75
,
,
,
,
,
,
Skylights Data (Table 2A, Construction Numbers 8-9) | [10 empty] | PSF
Const. No. | Description | Frame Construction |  | Ueff | SHGC | U-Curb | U-Shaft |  |  |  | North | NE/NW | E/W | SE/SW | South
8cuf-c | Flat generic skylight 1/4" glass | Metal sash no break (U=1.13) | 8cuf-c Flat generic skylight 1/4" glass, Metal sash no break (U=1.13) | 1.13 | 0.74 | 1.1 | 0.47 |  |  |  | 140.75 | 260.75 | 218.5 | 140.75 | 184.75
,
,
,
,
,
Doors Data (Table 4A, Construction Number 11)
Const. No. | Description |  |  | U-Value
11J | Metal, Fiberglass Core |  | 11J Metal, Fiberglass Core | 0.6
11S | Overhead Door, Wood Panels or Sections |  | 11S Overhead Door, Wood Panels or Sections | 0.78
Walls Data (Table 4A, Construction Numbers 12-15)
Const. No. | Description |  |  | U-Value | Group |  |  | Code
14F11-0-m | 4 inch concrete wall, Metal studs, R-11 cavity |  | 14F11-0-m 4 inch concrete wall, Metal studs, R-11 cavity | 0.148 | H |  |  | H15 | 14
12B-0s-m | Frame wall, Metal studs, R-11 cavity, wood sheathing, siding |  | 12B-0s-m Frame wall, Metal studs, R-11 cavity, wood sheathing, siding | 0.122 | B |  |  | B15 | 12
13CB-0fc | Block, Framing w/ R-13 cavity, drywall |  | 13CB-0fc Block, Framing w/ R-13 cavity, drywall | 0.073 | I |  |  | I15 | 13
13A-5oc-b | Block, brick exterior finish, R-5 insulation, open core, plus interior finish |  | 13A-5oc-b Block, brick exterior finish, R-5 insulation, open core, plus interior finish | 0.129 | F |  |  | F15 | 13
13AA-0occ | Block, no exterior or interior finish, core filled |  | 13AA-0occ Block, no exterior or interior finish, core filled | 0.304 | E |  |  | E15 | 13
12E-Osm | Frame wall, Metal studs, R-11 cavity, wood sheathing, siding |  | 12E-Osm Frame wall, Metal studs, R-11 cavity, wood sheathing, siding | 0.103 | E |  |  | E15 | 12
15
15
15
Ceilings Data (Table 4A, Construction Numbers 16-18)
Const. No. | Description |  |  | U-Value | Group |  |  | Code
17B-15m-19 | Metal deck plus R-15 board, R19 Suspended Ceiling |  | 17B-15m-19 Metal deck plus R-15 board, R19 Suspended Ceiling | 0.027 | RC13 |  |  | RC13 | 17
17B-10w | R-13 roof decking, dead air space, R-19 ceiling |  | 17B-10w R-13 roof decking, dead air space, R-19 ceiling | 0.022 | RC6 |  |  | RC6 | 17
17A -10pc | Concrete deck four inches thick r-12 board |  | 17A -10pc Concrete deck four inches thick r-12 board | 0.078 | RC12 |  |  | RC12 | 17
17B-10c-4lw | Concrete deck, 4 inch light weight, R10 board |  | 17B-10c-4lw Concrete deck, 4 inch light weight, R10 board | 0.063 | RC4 |  |  | RC4 | 17
17A-15m | Metal deck plus R-15 board, no ceiling |  | 17A-15m Metal deck plus R-15 board, no ceiling | 0.061 | R13 |  |  | R13 | 17
0
0
0
0
Floors (Table 4A, Construction Numbers 19-22)
Const. No. 19 | Description |  |  | U-Value | PTDH | PTDC
19AP-0c | No Wall Insulation, Vented Crawlspace, No Floor Insulation, Carpet |  | 19AP-0c No Wall Insulation, Vented Crawlspace, No Floor Insulation, Carpet | 0.368 | 24.4 | 7.5 |  |  | 19
20BP-0pc | Precast hollow core deck, no insulation |  | 20BP-0pc Precast hollow core deck, no insulation | 0.49 | 0 | 20 |  |  | 20
Const. No. 20A | Description |  |  | U-Value |  | CLTD
20AP-19 | Light Weight, Open Crawlspace, R-19 Floor Insulation |  | 20AP-19 Light Weight, Open Crawlspace, R-19 Floor Insulation | 0.05 |  | 15 |  |  | 20
Const. No. 20B | Description |  |  | U-Value |  | Group |  | CLTD
20BP-3CF-19 | 3" Cement-Fiber Slab, R-19 Blanket below Floor |  | 20BP-3CF-19 3" Cement-Fiber Slab, R-19 Blanket below Floor | 0.034 |  | CF5 |  | 12 | 20
20BP-0pc | Precast hollow core deck, no insulation |  | 20BP-0pc Precast hollow core deck, no insulation | 0.49 |  | CF3 |  | 15 | 20
#N/A
Const. No. 21 | Description |  |  | U-Value
21A-20 | Basement, R-0 |  | 21A-20 Basement, R-0 | 0.027
Const. No. 22 | Description |  |  | F-Value
22A-ph | Slab on Grade, No Edge Insulation, Light Wet Soil |  | 22A-ph Slab on Grade, No Edge Insulation, Light Wet Soil | 1.18
22B-10pm | Slab on grade, 2" Edge Insulation, Heavy Dry or Light Wet Soil |  | 22B-10pm Slab on grade, 2" Edge Insulation, Heavy Dry or Light Wet Soil | 0.355 |  |  |  |  | 22

## Wrk A (hidden)
Worksheet A Location and Design Conditions
Project Name: |  | Maria's Rest. Zone 1 |  |  |  | Room, Zone, or Block |  | Latitude | Elevation | ACF
City, State: |  | Long Beach Daughtery Field, California |  |  |  | Zone |  | 34 | 39 | 1
Default Design Conditions | Design Conditions for Heating |  |  |  | Midsummer Design Conditions for Cooling
| Dry-Bulb | Percent (1) | Table 12 (1) | Wind (5) | Dry-Bulb | MCWB | Percent | Design | Daily (4) | Wind (5)
| °F | %RH | Grains | MPH | °F | °F | %RH | Grains | Range | MPH
|  | DF = Blank | Optional | DF = 15.0 |  |  | DF = 50 |  | DR | DF = 7.5
Indoor Design | 70 |  |  | ~ | 75 | ~ | 50 | ~ | ~ | ~
Outdoor Values | 44 | 80 |  | 15 | 88 | 67 | ~ | 3 | 20 | 7.5
Month of Year (6) Conditions for Cooling | Month | Table 1C |  |  |  |  | Indoor | Hour of Day | Hour | HTA
| Jul & Aug | Index (%) | Dry-Bulb | Wet-Bulb | DR °F | Mo ΔGrains | Dry Bulb | Adjustment | of Day
|  | 1% | 88 | 67 | 20 | 3 | 75 | Table 1D-2 | 15:00 | 0
Cooling DB (6) and ΔGrains for Month / Hour | Month | Daily (4) | HTA | Load Time |  | Mo / Hr | Mo / Hour | Mo/Hour DB = Month DB - DR x HTA Mo/Hour ΔGarins = Month ΔGrains
| Dry-Bulb | Range |  | Month | Hour | Dry-Bulb | Δ Grains
| 88 | 20 | 0 | Jul & Aug | 0.625 | 88 | 3
Design Values for Temperature Difference and Grains Difference | Heating | [5 empty] | Cooling
| Dry-Bulb Difference °F |  | Grains (1) Difference |  |  |  | Dry-Bulb Difference °F |  | Design | Daily (4)
[9 empty] | Grains | Range °F
| Indoor | 70 | Indoor | 0 |  |  | Outdoor | 88 | 3 | 20
| Outdoor | 44 | Outdoor | 0 |  |  | Indoor | 75
| HTD | 26 | ΔGrains | 0 |  |  | CTD | 13
1) Grains Difference calculations for heating are used to calculate the winter humidification load (ignore if there is no winter humidification).
2) Output from altitude sensitive, state point psychometric software may be substituted for Table 12 Grains values.
3) Appendix 11 provides equations for altitude sensitive psychometrics.
4) Use daily range (DR) from Table 1C (preferred), or use default value for Table 1 daily range ( Low = 10° F; Medium = 20 °F and High = 30 °F).
5) Default wind speed is 15.0 MPH for heating and 7.5 MPH for cooling, or use engineered values.
6) Not supported by N5AP, use default design conditions for midsummer load estimates (use the full Manual N procedure for other months).
Table 1D-2 | Hour of Day Adjustment for Outdoor Temperature | [9 empty] | Altitude Correction (ACF)
| Unabridged Cooling Load Procedure | [9 empty] | For the Sensible and Latent Heat Equations
| Hour of | Hour of | Adjustment |  | Hour of | Hour of | Adjustment |  | Coincident
| Day | Day | Factor |  | Day | Day | Factor |  | Design |  | Specific heat of air approximately 0.24 Btu/Lb.
|  | (ST) | HTA |  |  | (ST) | HTA |  | Grains |  | Latent heat of condensation = 1,076 Btuh/Lb.
| 1 | 1:00 | 0.87 |  | 13 | 13:00 | 0.11 |  | Design Grains value for month of year applies to all hours of day. |  | Altitude | ACF | Altitude | ACF
| 2 | 2:00 | 0.92 |  | 14 | 14:00 | 0.03 |  |  |  | Sea Level | 1 | 6000 | 0.8
| 3 | 3:00 | 0.96 |  | 15 | 15:00 | 0 |  |  |  | 1000 | 0.97 | 7000 | 0.77
| 4 | 4:00 | 0.99 |  | 16 | 16:00 | 0.03 |  |  |  | 2000 | 0.93 | 8000 | 0.75
| 5 | 5:00 | 1 |  | 17 | 17:00 | 0.1 |  |  |  | 3000 | 0.89 | 9000 | 0.72
| 6 | 6:00 | 0.98 |  | 18 | 18:00 | 0.21 |  |  |  | 4000 | 0.87 | 10000 | 0.69
| 7 | 7:00 | 0.93 |  | 19 | 19:00 | 0.34 |  |  |  | 5000 | 0.84 | 12000 | 0.63
| 8 | 8:00 | 0.84 |  | 20 | 20:00 | 0.47
| 9 | 9:00 | 0.71 |  | 21 | 21:00 | 0.58
| 10 | 10:00 | 0.56 |  | 22 | 22:00 | 0.68
| 11 | 11:00 | 0.39 |  | 23 | 23:00 | 0.76
| 12 | Noon | 0.23 |  | 24 | Midnight | 0.82
Procedure (performed on Worksheet A):
1) Obtain design values for outdoor drybulb temperature(OATmo), Daily Range (DRmo) and Design Grains (DGmo) for month.
2) Use Table 1D-2 to obtain a HTA value forthe hour of interest (Standard Time = Daylight Savings Time - 1).
3) Outdoor drybulb temperature for month and hour of interest = OATmo,hr = OATmo - DRmo x HTA
4) Numerical equivalents for Daily Range: Low = 10° F; Medium = 20 °F; High = 30 °F
5) Design Grains value for hour of interest = DGmo

## Wrk C (hidden)
Worksheet C HTM Values for Skylights
Part 1 -- Construction Data
Attributes of skylight glazing assembly, curb and light shaft components.
Month |  | Hour | Latitude | HTD | CTD + 15 | Weight | [6 empty] | Type of space load (room #, zone # or block) > | Zone
Jul & Aug |  | 15:00 | 34 | 26 | 28 |  | Curb and Light Shaft Detals |  |  |  | Assembly Performance |  | Glazing Performance |  |  | SHGC Summary
Description of Assembly (optional) |  | Const. | Glazing | Curb Dimensions |  |  | Curb Size | Curb | Light Shaft | Light Shaft | Defaults for GP Glass |  | Defaults for CU Glass |  |  | SHGC | SHGC | SHGC
|  | Number | (Type) | Height | Length | Width | Table 2B-4 | Material | Material | Height (Ft) | GP Ueff | GP SHGC | Table 2C #8 or #9 |  |  | for | for | for
|  | & Room No. | Faces | H (In) | L (FT) | W (FT) |  | and R-value | and R-value | DF = 5.0 Ft | Table 2A | Table 2A | Upanel | CU SHGC |  | GP Glass | CU Glass | NFRC Glass
a |  | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  |  |  | a |  |  | ~
b |  | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  |  |  | b |  |  | ~
c |  | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  |  |  | c |  |  | ~
d |  | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  |  |  | d |  |  | ~
e |  | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  |  |  | e |  |  | ~
Provide line input for general purpose (GP) glass or commercial use (CU) glass (either, or). For NFRC glass, ignore line input for GP glass and CU glass. See Table 2A for GP glass or Table 3C for CU glass (Construction 8 for flat glazing or Construction 9 for dome glazing).
Part 2 — Use Default Ueff Value for GP Skylight, Curb and Light Shaft Assembly or Compute Actual Ueff
Enter Part 1 Ueff default; or use actual U-values and AR values (default AR or actual AR) to calculate Ueff for the complete assembly
Ueff Summary
Part 1 Line |  | Actual Performance |  | Curb | A-Panel | Curb Area Ratio |  | Shaft Area Ratio |  | Asm'bly | NFRC Rating |  |  | Asm'bly |  | Asm'bly | Asm'bly | Asm'bly
|  | or Table 2B-3 Default |  | Perim’ | L x W | A-Curb | ARcurb | A-Shaft | ARshaft | Ueff for | U-Value | NFRC | Includes | Ueff for |  | Ueff for | Ueff for | Ueff for
|  | U-Curb | U-Shaft | P (Ft) | SqFt |  |  |  |  | CU Glass |  | SHGC | Curb = 1 | NFRC Glass |  | GP Glass | CU Glass | NFRC Glass
a |  |  |  | 0 | 0 | 0 | #DIV/0! | 0 | #DIV/0! | #VALUE! |  |  |  | 0 | a |  | #VALUE! | ~
b |  |  |  | 0 | 0 | 0 | #DIV/0! | 0 | #DIV/0! | #VALUE! |  |  |  | 0 | b |  | #VALUE! | ~
c |  |  |  | 0 | 0 | 0 | #DIV/0! | 0 | #DIV/0! | #VALUE! |  |  |  | 0 | c |  | #VALUE! | ~
d |  |  |  | 0 | 0 | 0 | #DIV/0! | 0 | #DIV/0! | #VALUE! |  |  |  | 0 | d |  | #VALUE! | ~
e |  |  |  | 0 | 0 | 0 | #DIV/0! | 0 | #DIV/0! | #VALUE! |  |  |  | 0 | e |  | #VALUE! | ~
U-values and AR values not required if Table 2A or 2C Ueff is used for Assembly Ueff.. Table 2B-3 AR Defaults: AR for small curb = 0.35; AR for large curb = 0.75; AR for lightshaft = 4.00
Equations for Part 1 and Part 2
Actual U-value = 1 / Actual Total R-value |  |  |  |  | Acurb (SqFt) = P x (Curb height in inches) / 12 |  |  |  |  | For CU: Ueff = Upanel + Ucurb x ARcurb + Usft x ARsft
P = Curb perimeter (Ft) = 2 x (L + W) |  |  |  |  | ARcurb = Acurb / Apanel |  |  |  |  | If NFRC Rating does not include curb:
Apanel (SqFt) = L x W |  |  |  |  | Ashaft (SqFt) = P x Shaft height in feet |  |  |  |  | Ueff = UNFRC + Ucurb x ARcurb + Usft x ARsft
[5 empty] | ARshaft = Ashaft / Apanel |  |  |  |  | Or with curb: Ueff = UNFRC + Usft x ARsft
Part 3 -- Calculate the Heating and Cooling HTM Values for the Skylight Assembly
Part 1 Line | Tilt | Horizontal |  |  |  | Vertical |  |  |  | GP, CU | ISC | GP, CU | HTM | HTM
| Angle | Cos Θ | PSF | CLF | Sol-H | Sine Θ | PSF | CLF | Sol-V | or NFRC | 3D-4 | or NFRC | Heat | Cool
| Θ |  | 3D-2 | 3D-3 |  |  | 3D-2 | 3D-3 |  | SHGC | DF = 1.0 | Ueff
a | 0 | 1 |  |  | #VALUE! | 0 |  |  | #VALUE! |  | 1 | #VALUE!
b | 0 | 1 |  |  | #VALUE! | 0 |  |  | #VALUE! |  | 1 | #VALUE!
c | 0 | 1 |  |  | #VALUE! | 0 |  |  | #VALUE! |  | 1 | #VALUE!
d | 0 | 1 |  |  | #VALUE! | 0 |  |  | #VALUE! |  | 1 | #VALUE!
e | 0 | 1 |  |  | #VALUE! | 0 |  |  | #VALUE! |  | 1 | #VALUE!
Equations for Part 3
Use Tables 3D-2 and 3D-3 to obtain horizontal and directional values for PSF and CLF. Use the CLF for no internal shade or for internal shade, as applicable. ISC values from Table 3D-4 may be used for skylights. | [6 empty] | SolH = Cos Θ x (PSF x CLF) Horizontal |  |  |  | Heat HTM = Ueff x HTD
[7 empty] | SolV = Sin Θ x (PSF x CLF) Vertical |  |  |  | Cool HTM = (SolH + SolV) x (SHGC / 0.87) x ISC
+ Ueff x (CTD +15)
ISC for no internal shade = 1.0
Export to Form N1: Heating HTMs, Cooling HTMs; and rough opening areas (Curb L x W).

## GlassI
Glass Information
| Construction Number & Description | Qty | Direction | Width |  | Heigth |  | Internal | Glass |  |  | Construction
|  |  |  | Ft | In | Ft | In | Shading | Adjustment |  |  | Weight | Sq. ft. | U-Value | SHGC | PSF | CLF
a | 1c-cuf-c Double pane, fixed sash, Metal no break | 1 | East | 20 | 0 | 8 | 0 | None | None |  |  | Medium | 160 | 0.69 | 0.63 | 218.5 | 0.29
b | 1c-cuf-c Double pane, fixed sash, Metal no break | 1 | East | 3 | 0 | 6 | 9 | None | None |  |  |  | 20.25 | 0.69 | 0.63 | 218.5 | 0.29
c | [7 empty] | None | None |  |  |  | 0
d | [7 empty] | None | None |  |  |  | 0
e | [7 empty] | None | None |  |  |  | 0
f | [7 empty] | None | None |  |  |  | 0
g | [7 empty] | None | None |  |  |  | 0
h | [7 empty] | None | None |  |  |  | 0
| Construction Number & Description |  | Overhang Adjustment |  | X = Overhang |  | Y = Top of
[5 empty] | Distance |  | Opening to |  |  | X |  |  | No
[7 empty] | Overhang | [5 empty] | Yes
[5 empty] | Ft | In | Ft | In
a | 1c-cuf-c Double pane, fixed sash, Metal no break |  | Yes |  | 4 | 0 | 2 | 0 |  |  | Y
b | 1c-cuf-c Double pane, fixed sash, Metal no break |  | Yes |  | 4 | 0 | 3 | 3
c | 0
d | 0
e | 0
f | 0
g | 0
h | 0
► Return to N1 Form

## Wrk B (hidden)
Worksheet B HTM Values for Windows and Glass Doors
Part 1 -- Basic HTM for Direction Glass Faces
Directional HTM with applicable adjustment for internal shade, insect screen and bay or garden window shape.
Not adjusted for overhang or external sun screen (see Part 2).
Month |  | Hour | Latitude | HTD | CTD | Weight | Type of space load (room #, zone # or block) > | [5 empty] | Zone
Jul & Aug |  | 15:00 | 34 | 26 | 13 |  | Table 3D Values |  |  | Heat | Cool | Bug Screen | AHTMD | Enter 1
Description of Assembly (optional) |  | Const. | Internal | Glazing | U-value | SHGC | PSF | CLF | ISC | HTM | HTMD | or Proj. Asy. |  | for
|  | Number | Shade | Direction | Tbl 2 or | Tbl 2 or | 3D-2 | 3D-3 | 3D-4 |  |  | Adjust |  | Sun Screen
|  | & Room No. | (Type) |  | NFRC | NFRC |  |  | DF= 0.80 |  |  | DF= 1.0 |  | DF = Blank | No | Yes
a | East | 1c-cuf-c Double pane, fixed sash, Metal no break | None | East | 0.69 | 0.63 | 218.5 | 0.29 | 1 | 17.94 | 54.855 | 1 | 54.855 |  | 54.855 | 54.855 | Yes | 54.855
b | East | 1c-cuf-c Double pane, fixed sash, Metal no break | None | East | 0.69 | 0.63 | 218.5 | 0.29 | 1 | 17.94 | 54.855 | 1 | 54.855 |  | 54.855 | 54.855 | Yes | 54.855
c | 0 | 0 | None | 0 |  |  |  |  | 1 |  |  | 1 |  |  |  | 0 | 0
d | 0 | 0 | None | 0 |  |  |  |  | 1 |  |  | 1 |  |  |  | 0 | 0
e | 0 | 0 | None | 0 |  |  |  |  | 1 |  |  | 1 |  |  |  | 0 | 0
f | 0 | 0 | None | 0 |  |  |  |  | 1 |  |  | 1 |  |  |  | 0 | 0
g | 0 | 0 | None | 0 |  |  |  |  | 1 |  |  | 1 |  |  |  | 0 | 0
h | 0 | 0 | None | 0 |  |  |  |  | 1 |  |  | 1 |  |  |  | 0 | 0
Part 2A -- Basic HTM for North Facing Glass
HTM for Part 1 glass facing North, with applicable adjustment for internal shade, insect screen and bay or garden window shape.
(Required for Part 2B Calculations)
Part 1 Line |  | Use these lines to generate HTMN values for Table 3E-1 or for the HTMss equation. |  | Faces | Part 1 | Part 1 | North | North | Part 1 |  | Cool | Part 1 | AHTMN
[5 empty] | Uvalue | SHGC | PSF | CLF | ISC |  | HTMN | Adjustment
[7 empty] | 3D-2 | 3D-3
a | East |  |  | North | 0.69 | 0.63 | 36.5 | 0.76 | 1 |  | 29.0576 | 1 | 29.0576
b | East |  |  |  | 0.69 | 0.63 | 36.5 | 0.76 | 1 |  | 29.0576 | 1 | 29.0576
c | 0 | [5 empty] | 0 | 0 | 1 |  |  | 1
d | 0 | [5 empty] | 0 | 0 | 1 |  |  | 1
e | 0 | [5 empty] | 0 | 0 | 1 |  |  | 1
f | 0 | [5 empty] | 0 | 0 | 1 |  |  | 1
g | 0 | [5 empty] | 0 | 0 | 1 |  |  | 1
h | 0 | [5 empty] | 0 | 0 | 1 |  |  | 1
Equations for Part 1 and Part 2A | [9 empty] | Insect screen adjustment: |  |  | Outdoor | Indoor
Heat HTM = U x HTD | [5 empty] | Default ISC Values: | [5 empty] | Full | 0.8 | 0.9
Cool HTMD = PSF x CLF x (SHGC / 0.87) x ISC + U x CTD | [5 empty] | No internal shade = 1.0 | [5 empty] | Half | 0.9 | 0.95
AHTMD = Cool HTMD x bug screen or projection adjustment | [5 empty] | Blinds @ 45o = 1.175 x Table 3D-4 value |  |  |  | French door adjustment = 0.70 (cooling only).
AHTMN = Cool HTMN x bug screen or projection adjustment | [5 empty] | R-shade @ ½ = 0.5 x (1.0 + 3D-4 value) |  |  |  | Bay window factor = 1.15
See Table 3E-3 for foreground reflectance option | [5 empty] | Drape @ ½ = 0.5 x (1.0 + 3D-4 value) |  |  |  | Garden window factor = 2.00
Part 2B -- HTM Adjusted for Overhang or External Sun Screen
[9 empty] | Month = | Jul & Aug | Time = | 0.625 | Lat = | 34
Part 1 Line |  | Sun Screen Adjustment |  |  |  | Overhang Adjustment
|  | HTMss = (HTMD - HTMN) x SCss+ HTMN |  |  |  | Use Table 3E-1 for HTMOH
|  | AHTMD | AHTMN | Shd. Coef. | HTMss | AHTMD | AHTMN | OH Proj | Above | Glass | Glass | Faces | SLM | HTMOH
|  |  |  | SCss |  |  |  | (X) Ft | Glass | Height | Width | and Mo | Table 3E
|  |  |  | DF = 1.0 |  |  |  |  | (Y) Ft | (H) Ft | (W) Ft | and Hour | @ Lat
a | East | 54.855 | 29.0576 | 1 | 54.855 | 54.855 | 29.0576 | 4 | 2 | 8 | 20 |  | 0 | 54.855
b | East | 54.855 | 29.0576 | 1 | 54.855 | 54.855 | 29.0576 | 4 | 3.25 | 6.75 | 3 |  | 0 | 54.855
c | 0 |  |  | 1 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0
d | 0 |  |  | 1 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0
e | 0 |  |  | 1 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0
f | 0 |  |  | 1 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0
g | 0 |  |  | 1 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0
h | 0 |  |  | 1 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0
Export to Form N1: Heating HTM; and AHTOH from Part 2B; and rough opening area (H x W).
Overhang Adjustment -- Table 3E-1 Worksheet
Line | Faces | Length | SLM | SL distance | To OH | Shd Ht | Opening | No shade Ht | Opening | Shade Area | Sun Area | AHTMD | AHTMN | Shaded | Sun Lit | Total | HTMOH
|  | X in Ft |  | Z = X x SLM | Y in Ft | S = Z - Y | High (FT) | U = H - S | Wide (FT) | S x W | U x W | See note |  | Load | Load | Load
a | East | 4 | 0 | 0 | 2 | 0 | 8 | 8 | 20 | 0 | 160 | 54.855 | 29.0576 | 0 | 8776.8 | 8776.8 | 54.855
b | East | 4 | 0 | 0 | 3.25 | 0 | 6.75 | 6.75 | 3 | 0 | 20.25 | 54.855 | 29.0576 | 0 | 1110.8138 | 1110.8138 | 54.855
c | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | #VALUE! | #VALUE! | #VALUE! | 0
d | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | #VALUE! | #VALUE! | #VALUE! | 0
e | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | #VALUE! | #VALUE! | #VALUE! | 0
f | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | #VALUE! | #VALUE! | #VALUE! | 0
g | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | #VALUE! | #VALUE! | #VALUE! | 0
h | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | #VALUE! | #VALUE! | #VALUE! | 0
Note: If item has a sun screen, AHTMD = SCss from Part 2B. If no sun screen, use AHTMD from part 1.
Note on K13: Doulble pane clear with medium blind at 45 degrees.

## SkylightI
Skylight Information
| Construction Number & Description | Direction | Light Dimensions |  | Curb | Tilt Angle ° | Light Shaft Height (FT) | Construction |  |  |  |  | PSF | CLF
|  |  | Length | Width | Height |  |  | Weight | Ueff | SHGC | PSF | CLF | Horizontal | Horizontal
|  |  | L (FT) | W (FT) | H (In) | [9 empty] | U-Curb | U-Shaft
a | [5 empty] | 0 |  | Medium
b | [5 empty] | 0
c
d
e
► Return to N1 Form

## DoorI
Doors Information
| Construction Number & Description | Direction | Net | Color
|  |  | Sq. ft. |  | U-Value
a |  |  |  | Default
b |  |  |  | Default
c
► Return to N1 Form

## WallI
Above Grade Walls Information
| Construction Number & Description | Net | Direction | Color
|  | Sq. ft. |  |  | U-Value | CLTD | Group# | Group
a | 13CB-0fc Block, Framing w/ R-13 cavity, drywall | 200 | West | Default | 0.073 | 25 | I15 | I
b |  |  |  | Default |  | #N/A
c |  |  |  | Default |  | #N/A
d |  |  |  | Default |  | #N/A
e | [5 empty] | #N/A
f | [5 empty] | #N/A
g | [5 empty] | #N/A
h | [5 empty] | #N/A
Partition Walls Information
| Construction Number & Description | Net | PTDH | PTDC
|  | Sq. ft. |  |  | U-Value
p1 | 13CB-0fc Block, Framing w/ R-13 cavity, drywall | 516 | 0 | 0 | 0.073
p2 | 12B-0s-m Frame wall, Metal studs, R-11 cavity, wood sheathing, siding | 396 | 0 | 5 | 0.122
► Return to N1 Form

## CeilingI
Ceilings Information
| Construction Number & Description | Sq. ft. | Color | U-Value | CLTD | Group | Color | Const. #
a | 17A-15m Metal deck plus R-15 board, no ceiling | 1117 | White | 0.061 | 33 | R13 | 0.78 | 17
b
c
► Return to N1 Form

## FloorI
Floors Information
| Construction Number 19 (Over Enclosed Space) & Description | Sq. ft. | U-Value | HTD | CLTD
a | [5 empty] | 19
b | [5 empty] | 19
| Construction Number 20A (Light Weight Over Open Space) & Description | Sq. ft.
c | [5 empty] | 20
| Construction Number 20B (Commercial Over Open Space) & Description | Sq. ft.
d | [5 empty] | 20
| Construction Number 21 (Basement Floor) & Description | Sq. ft.
e
| Construction Number 22 (Concrete Slab on Grade) & Description | Perimeter
f | 22B-10pm Slab on grade, 2" Edge Insulation, Heavy Dry or Light Wet Soil | 116 | 0.355
► Return to N1 Form

## InternalI
Internal Loads
Lighting Fixtures
Qty | FixtureWatts |  |  |  | DF
1 | 1005 |  |  |  | 1
Occupants
Qty | Activity |  |  |  | DF | Sens. | Latent
58 | Seated, eating a meal |  |  |  | 0.9 | 275 | 275
12 | Seated, bar or conference room |  |  |  | 0.9 | 245 | 155
4 | Standing, light work |  |  |  |  | 250 | 200
Office Equipment
Qty | Watts | or | BTUH | Latent Value | DF
[6 empty] | Sens. | Latent
2 |  | or | 200 | 0 | 0.5 | 200 | 0
1 | 35 | or |  |  | 0.5 | 54.25 | 0
1 | 20 | or |  |  | 0.5 | 31 | 0
|  | or |  |  |  | 0 | 0 | 285.25 | 0
Food Service Equipment and
Investigated Loads
Qty | Watts | or | BTUH | Latent Value | DF
[6 empty] | Sens. | Latent
1 |  | or | 11076 | 2310 | 0.5 | 5538 | 1155
1 |  | or | 1076 | 5180 | 0.5 | 538 | 2590
|  | or |  |  |  | 0 | 0
|  | or |  |  |  | 0 | 0 | 6076 | 3745
Plants
Qty | Size
Small
Medium
Large
Blower Heat
[8 empty] | SA | RA
[6 empty] | 2 | 0 | 2016.602 | 1008.301
[7 empty] | 2016.602 | 2016.602
[6 empty] | FALSE | 0
TRUE
►Return to N1 Form | [6 empty] | 0
Draw Thru Blower
Blow Thru Blower
Additional Return Fan
Blower Heat Included in OEM Data

## DuctsI
Ducts
|  |  | 7RC | Radial or Spider Supply and Return System Installed in a Unconditioned Space or Outdoors, Center Supply Outlets | 7RC Radial or Spider Supply and Return System Installed in a Unconditioned Space or Outdoors, Center Supply Outlets | 1 | #N/A
Duct Insulation | Leakage Class |  | 7RP | Radial or Spider Supply and Return System Installed in a Unconditioned Space or Outdoors, Perimeter Supply Outlets | 7RP Radial or Spider Supply and Return System Installed in a Unconditioned Space or Outdoors, Perimeter Supply Outlets | 2
Installed Square Feet of Supply Duct or Default = "T" |  | T | 7TC | Trunk and Branch Supply and Return System Installed in a Unconditioned Space or Outdoors, Center Supply Outlets | 7TC Trunk and Branch Supply and Return System Installed in a Unconditioned Space or Outdoors, Center Supply Outlets | 3
Installed Square Feet of Return Duct or Default = "T" |  | T | 7TP | Trunk and Branch Supply and Return System Installed in a Unconditioned Space or Outdoors, Perimeter Supply Outlets | 7TP Trunk and Branch Supply and Return System Installed in a Unconditioned Space or Outdoors, Perimeter Supply Outlets | 4
Ambient Temperature for Duct Location (Heating) |  |  | 7GSC | Radial or Spider Supply System Installed Under a Ground Slab, Return in Conditioned Space | 7GSC Radial or Spider Supply System Installed Under a Ground Slab, Return in Conditioned Space | 5
Ambient Temperature for Duct Location (Cooling)
►Return to N1 Form

## InfiltrationI
Infiltration
Levels | Exposure | Tightness
Single Story | 1 or 2 Exposures | Average
Door Traffic for Normal Use Door
Code Description |  |  | TR
5F-ssd-nv Single Swinging Door (21 SqFt), no vestibule |  |  | 25
Code Description |  |  | RPM
5F-ard Motorized Revolving Door |  |  | 0
TR = Total Entrances and Exits Per Door Per Hour
Overhead Door Infiltration
Code Description |  |  |  | TR | Sq. Ft.
TR = Operating Cycles Per Door Per Hour
►Return to N1 Form

## DuctsT (hidden)
#N/A | #N/A | #N/A
| #N/A | #N/A | [17 empty] | #N/A | #N/A | [11 empty] | #N/A | #N/A
| #N/A | 0 | 3750 | 4500 | 5250 | 6000 | 6750 | 7500 | 8250 | 9000 | 9750 | 10500 | 11250 | 12000 | 12750 | 13500 | 14250 | 15000 |  |  | 0 | 3750 | 4500 | 5250 | 6000 | 7500 | 9000 | 10500 | 12000 | 13500 | 15000 |  |  | 0 | 3750 | 4500 | 5250 | 6000 | 6750 | 7500 | 8250 | 9000 | 9750 | 10500 | 11250 | 12000 | 13500 | 15000
| -20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| -15 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 65 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 15 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| -10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 70 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| -5 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 75 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 25 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 80 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| 5 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 85 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 35 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 90 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 40 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| 15 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 95 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 45 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| 25 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 105 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 55 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 110 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| 35 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 115 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 65 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| 40 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 120 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 70 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| 45 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 125 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 3 | 1117 | #N/A
| 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 130 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| 55 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 135 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 140 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| 65 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 145 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| 70 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | 150 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| 0 | 1117 | #N/A | [16 empty] | 160 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[20 empty] | 0 | 1117 | #N/A
| #N/A | [6 empty] | #N/A | [5 empty] | ALF for Duct Table
|  | #N/A | #N/A | #N/A |  |  |  |  | #N/A | #N/A | #N/A |  |  | 1.6412 | 0 | 1 | 0.5 | 1.5
|  | #N/A | #N/A | [5 empty] | #N/A | #N/A |  |  |  |  | 0.75 | 2 | 1 | 3
|  | #N/A | #N/A | [5 empty] | #N/A | #N/A |  |  |  |  | 1.25 | 3 | 1.5
|  | #N/A | #N/A | [5 empty] | #N/A | #N/A |  |  |  |  | 1.75 | 4 | 2
[15 empty] | 2 |  | 2
| #N/A | [6 empty] | #N/A | [19 empty] | #N/A
|  | #N/A | #N/A | #N/A | #N/A |  |  |  | R2 | R4 | R6 | R8 | [6 empty] | 0 | [9 empty] | R2 | R4 | R6 | R8
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | Tight | 0.06 / 0.06 Tight |  | 0.06 / 0.06 | #N/A | [8 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | Semi-Tight | 0.09 / 0.15 Semi-Tight |  | 0.09 / 0.15 | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | Average | 0.12 / 0.24 Average |  | 0.12 / 0.24 | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | Semi-Loose | 0.24 / 0.47 Semi-Loose |  | 0.24 / 0.47 | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | Loose | 0.35 / 0.70 Loose |  | 0.35 / 0.70 | [9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
#N/A
| #N/A |  |  | Supply
| 0 | 3750 | 4500 | 5250 | 6000 | 6750 | 7500 | 8250 | 9000 | 9750 | 10500 | 11250 | 12000 | 12750 | 13500 | 14250 | 15000 |  | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A
| #N/A | [17 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
[19 empty] | #N/A | #N/A | #N/A
| #N/A |  |  | Return | [14 empty] | #N/A | #N/A | #N/A
| 0 | 3750 | 4500 | 5250 | 6000 | 6750 | 7500 | 8250 | 9000 | 9750 | 10500 | 11250 | 12000 | 12750 | 13500 | 14250 | 15000 |  | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A
#N/A
[27 empty] | ALF | Radial or Spider Supply and Return System Installed in a Unconditioned Space or Outdoors | [23 empty] | Table |  | ALF | Radial or Spider Supply and Return System Installed in a Unconditioned Space or Outdoors | [16 empty] | Table |  | ALF | Radial or Spider Supply and Return System Installed in a Unconditioned Space or Outdoors | [16 empty] | Table |  | ALF | Radial or Spider Supply and Return System Installed in a Unconditioned Space or Outdoors | [16 empty] | Table
[27 empty] | 0.50 | Supply location = Center of room ceilings |  |  |  | Number of supplies: 3,000 SF = 15; 6,000 SF = 20; 9,000 SF = 25; 12,000 SF = 30; 15,000 SF = 35 | [13 empty] | One return for four supplies; returns close to air handler | [5 empty] | 7RC-0.50 |  | 1.0 | Supply location = Center of room ceilings |  |  |  | Number of supplies: 3,000 SF = 15; 6,000 SF = 20; 9,000 SF = 25; 12,000 SF = 30; 15,000 SF = 35 | [7 empty] | One return for four supplies; returns close to air handler |  |  |  |  | 7RC-1.0 |  | 1.5 | Supply location = Center of room ceilings |  |  |  | Number of supplies: 3,000 SF = 15; 6,000 SF = 20; 9,000 SF = 25; 12,000 SF = 30; 15,000 SF = 35 | [7 empty] | One return for four supplies; returns close to air handler |  |  |  |  | 7RC-1.5 |  | 2.0 | Supply location = Center of room ceilings |  |  |  | Number of supplies: 3,000 SF = 15; 6,000 SF = 20; 9,000 SF = 25; 12,000 SF = 30; 15,000 SF = 35 | [7 empty] | One return for four supplies; returns close to air handler |  |  |  |  | 7RC-2.0
[28 empty] | Duct leakage Cfm per SqFt of duct surface area (supply / return) = 0.06/0.06; 0.09/0.15; 0.12/0.24; 0.24/0.47; 0.35/0.70 | [17 empty] | Duct wall insulation R-value = 2, 4, 6 and 8 | [8 empty] | Duct leakage Cfm per SqFt of duct surface area (supply / return) = 0.06/0.06; 0.09/0.15; 0.12/0.24; 0.24/0.47; 0.35/0.70 | [11 empty] | Duct wall insulation R-value = 2, 4, 6 and 8 | [7 empty] | Duct leakage Cfm per SqFt of duct surface area (supply / return) = 0.06/0.06; 0.09/0.15; 0.12/0.24; 0.24/0.47; 0.35/0.70 | [11 empty] | Duct wall insulation R-value = 2, 4, 6 and 8 | [7 empty] | Duct leakage Cfm per SqFt of duct surface area (supply / return) = 0.06/0.06; 0.09/0.15; 0.12/0.24; 0.24/0.47; 0.35/0.70 | [11 empty] | Duct wall insulation R-value = 2, 4, 6 and 8
[27 empty] | Base Case Heat Loss Factor (BHLF) | [6 empty] | Base Case Sensible Gain Factor (BSGF) | [13 empty] | ± Btuh Values for Base Case Latent Gain (BLG) | [5 empty] | Base Case Heat Loss Factor (BHLF) | [6 empty] | Base Case Sensible Gain Factor (BSGF) | [6 empty] | ± Btuh Values for Base Case Latent Gain (BLG) | [5 empty] | Base Case Heat Loss Factor (BHLF) | [6 empty] | Base Case Sensible Gain Factor (BSGF) | [6 empty] | Base Case Latent Gain (BLG) | [5 empty] | Base Case Heat Loss Factor (BHLF) | [6 empty] | Base Case Sensible Gain Factor (BSGF) | [6 empty] | ± Btuh Values for Base Case Latent Gain (BLG)
3 | 7RC-1.5 | Radial or Spider Supply and Return System Installed in a Unconditioned Space or Outdoors, Center Supply Outlets | [24 empty] | R6 Insulation, ASHRAE Sealed (Supply = 0.12, Return = 0.24) | [6 empty] | R6 Insulation, ASHRAE Sealed (Supply = 0.12, Return = 0.24) | [13 empty] | R6 Insulation, ASHRAE Sealed (Supply = 0.12, Return = 0.24) | [5 empty] | R6 Insulation, ASHRAE Sealed (Supply = 0.12, Return = 0.24) | [6 empty] | R6 Insulation, ASHRAE Sealed (Supply = 0.12, Return = 0.24) | [6 empty] | R6 Insulation, ASHRAE Sealed (Supply = 0.12, Return = 0.24) | [5 empty] | R6 Insulation, ASHRAE Sealed (Supply = 0.12, Return = 0.24) | [6 empty] | R6 Insulation, ASHRAE Sealed (Supply = 0.12, Return = 0.24) | [6 empty] | R6 Insulation, ASHRAE Sealed (Supply = 0.12, Return = 0.24) | [5 empty] | R6 Insulation, ASHRAE Sealed (Supply = 0.12, Return = 0.24) | [6 empty] | R6 Insulation, ASHRAE Sealed (Supply = 0.12, Return = 0.24) | [6 empty] | R6 Insulation, ASHRAE Sealed (Supply = 0.12, Return = 0.24)
| Ambient | Square Feet of Floor Area | [5 empty] | Ambient | Square Feet of Floor Area | [5 empty] | Ambient | Square Feet of Floor Area | [10 empty] | Ambient | Square Feet of Floor Area | [5 empty] | Ambient |  | Square Feet of Floor Area | [11 empty] | Ambient | Square Feet of Floor Area |  |  |  |  | Ambient | Square Feet of Floor Area | [5 empty] | Ambient | Square Feet of Floor Area | [5 empty] | Ambient | Square Feet of Floor Area |  |  |  |  | Ambient | Square Feet of Floor Area | [5 empty] | Ambient | Square Feet of Floor Area | [5 empty] | Ambient | Square Feet of Floor Area |  |  |  |  | Ambient | Square Feet of Floor Area | [5 empty] | Ambient | Square Feet of Floor Area | [5 empty] | Ambient | Square Feet of Floor Area
| Dry Bulb | 3000 | 6000 | 9000 | 12000 | 15000 |  | Dry Bulb | 3000 | 6000 | 9000 | 12000 | 15000 |  | Grains | 3000 | 6000 | 9000 | 12000 | 15000 | [6 empty] | Dry Bulb | 3000 | 6000 | 9000 | 12000 | 15000 |  | Dry Bulb |  | 3000 |  | 6000 |  | 9000 |  | 12000 |  | 15000 |  |  |  | ∆ Grains ± | 3000 | 6000 | 9000 | 12000 | 15000 | Dry Bulb | 3000 | 6000 | 9000 | 12000 | 15000 |  | Dry Bulb | 3000 | 6000 | 9000 | 12000 | 15000 |  | ∆ Grains ± | 3000 | 6000 | 9000 | 12000 | 15000 | Dry Bulb | 3000 | 6000 | 9000 | 12000 | 15000 |  | Dry Bulb | 3000 | 6000 | 9000 | 12000 | 15000 |  | Grains | 3000 | 6000 | 9000 | 12000 | 15000 | Dry Bulb | 3000 | 6000 | 9000 | 12000 | 15000 |  | Dry Bulb | 3000 | 6000 | 9000 | 12000 | 15000 |  | ∆ Grains ± | 3000 | 6000 | 9000 | 12000 | 15000
| -20 | 0.12025 | 0.13319 | 0.14613 | 0.15906 | 0.172 |  | 60 | 0.002 | 0.002625 | 0.00325 | 0.003875 | 0.0045 |  | 10 | 1287 | 3298.25 | 5309.5 | 7320.75 | 9332 | [6 empty] | -20 | 0.2085 | 0.22937 | 0.25025 | 0.27113 | 0.292 |  | 60 |  | 0.007 |  | 0.00775 |  | 0.0085 |  | 0.00925 |  | 0.01 |  |  |  | 10 | 362 | 936 | 1510 | 2084 | 2658 | -20 | 0.136 | 0.1505 | 0.165 | 0.1795 | 0.194 |  | 60 | 0.002 | 0.00275 | 0.0035 | 0.00425 | 0.005 |  | 10 | 1944 | 4989.25 | 8034.5 | 11079.75 | 14125 | -20 | 0.12025 | 0.13319 | 0.14613 | 0.15906 | 0.172 |  | 60 | 0.002 | 0.002625 | 0.00325 | 0.003875 | 0.0045 |  | 10 | 1287 | 3298.25 | 5309.5 | 7320.75 | 9332 | -20 | 0.1045 | 0.11588 | 0.12725 | 0.13862 | 0.15 |  | 60 | 0.002 | 0.0025 | 0.003 | 0.0035 | 0.004 |  | 10 | 630 | 1607.25 | 2584.5 | 3561.75 | 4539
| -10 | 0.10967 | 0.1215 | 0.13333 | 0.14517 | 0.157 |  | 70 | 0.016503 | 0.018815 | 0.021128 | 0.02344 | 0.025753 |  | 20 | 1518.1667 | 3873 | 6227.8333 | 8582.6667 | 10937.5 | [6 empty] | -10 | 0.19067 | 0.20975 | 0.22883 | 0.24792 | 0.267 |  | 70 |  | 0.0338 |  | 0.0371 |  | 0.0404 |  | 0.0437 |  | 0.047 |  |  |  | 20 | 549.3333 | 1418.9583 | 2288.5833 | 3158.2083 | 4027.8333 | -10 | 0.124 | 0.13725 | 0.1505 | 0.16375 | 0.177 |  | 70 | 0.0191 | 0.0218 | 0.0245 | 0.0272 | 0.0299 |  | 20 | 2065.6667 | 5282.1667 | 8498.6667 | 11715.1667 | 14931.6667 | -10 | 0.10967 | 0.1215 | 0.13333 | 0.14517 | 0.157 |  | 70 | 0.016503 | 0.018815 | 0.021128 | 0.02344 | 0.025753 |  | 20 | 1518.1667 | 3873 | 6227.8333 | 8582.6667 | 10937.5 | -10 | 0.095333 | 0.10575 | 0.11617 | 0.12658 | 0.137 |  | 70 | 0.013905 | 0.01583 | 0.017755 | 0.01968 | 0.021605 |  | 20 | 970.6667 | 2463.8333 | 3957 | 5450.1667 | 6943.3333
| 0 | 0.099083 | 0.10981 | 0.12054 | 0.13127 | 0.142 |  | 80 | 0.031005 | 0.035005 | 0.039005 | 0.043005 | 0.047006 |  | 30 | 1749.3333 | 4447.75 | 7146.1667 | 9844.5833 | 12543 | [6 empty] | 0 | 0.17283 | 0.19013 | 0.20742 | 0.22471 | 0.242 |  | 80 |  | 0.0606 |  | 0.06645 |  | 0.0723 |  | 0.07815 |  | 0.084 |  |  |  | 30 | 736.6667 | 1901.9167 | 3067.1667 | 4232.4167 | 5397.6667 | 0 | 0.112 | 0.124 | 0.136 | 0.148 | 0.16 |  | 80 | 0.0362 | 0.04085 | 0.0455 | 0.05015 | 0.0548 |  | 30 | 2187.3333 | 5575.0833 | 8962.8333 | 12350.5833 | 15738.3333 | 0 | 0.099083 | 0.10981 | 0.12054 | 0.13127 | 0.142 |  | 80 | 0.031005 | 0.035005 | 0.039005 | 0.043005 | 0.047006 |  | 30 | 1749.3333 | 4447.75 | 7146.1667 | 9844.5833 | 12543 | 0 | 0.086167 | 0.095625 | 0.10508 | 0.11454 | 0.124 |  | 80 | 0.02581 | 0.02916 | 0.032511 | 0.035861 | 0.039211 |  | 30 | 1311.3333 | 3320.4167 | 5329.5 | 7338.5833 | 9347.6667
| 10 | 0.0885 | 0.098125 | 0.10775 | 0.11737 | 0.127 |  | 90 | 0.045508 | 0.051195 | 0.056883 | 0.062571 | 0.068258 |  | 40 | 1980.5 | 5022.5 | 8064.5 | 11106.5 | 14148.5 | [6 empty] | 10 | 0.155 | 0.1705 | 0.186 | 0.2015 | 0.217 |  | 90 |  | 0.0874 |  | 0.0958 |  | 0.1042 |  | 0.1126 |  | 0.121 |  |  |  | 40 | 924 | 2384.875 | 3845.75 | 5306.625 | 6767.5 | 10 | 0.1 | 0.11075 | 0.1215 | 0.13225 | 0.143 |  | 90 | 0.0533 | 0.0599 | 0.0665 | 0.0731 | 0.0797 |  | 40 | 2309 | 5868 | 9427 | 12986 | 16545 | 10 | 0.0885 | 0.098125 | 0.10775 | 0.11737 | 0.127 |  | 90 | 0.045508 | 0.051195 | 0.056883 | 0.062571 | 0.068258 |  | 40 | 1980.5 | 5022.5 | 8064.5 | 11106.5 | 14148.5 | 10 | 0.077 | 0.0855 | 0.094 | 0.1025 | 0.111 |  | 90 | 0.037715 | 0.042491 | 0.047266 | 0.052041 | 0.056816 |  | 40 | 1652 | 4177 | 6702 | 9227 | 11752
| 20 | 0.077917 | 0.086438 | 0.094958 | 0.10348 | 0.112 |  | 100 | 0.06001 | 0.067385 | 0.074761 | 0.082136 | 0.089511 |  | 50 | 2211.6667 | 5597.25 | 8982.8333 | 12368.4167 | 15754 | [6 empty] | 20 | 0.13717 | 0.15088 | 0.16458 | 0.17829 | 0.192 |  | 100 |  | 0.1142 |  | 0.12515 |  | 0.1361 |  | 0.14705 |  | 0.158 |  |  |  | 50 | 1111.3333 | 2867.8333 | 4624.3333 | 6380.8333 | 8137.3333 | 20 | 0.088 | 0.0975 | 0.107 | 0.1165 | 0.126 |  | 100 | 0.0704 | 0.07895 | 0.0875 | 0.09605 | 0.1046 |  | 50 | 2430.6667 | 6160.9167 | 9891.1667 | 13621.4167 | 17351.6667 | 20 | 0.077917 | 0.086438 | 0.094958 | 0.10348 | 0.112 |  | 100 | 0.06001 | 0.067385 | 0.074761 | 0.082136 | 0.089511 |  | 50 | 2211.6667 | 5597.25 | 8982.8333 | 12368.4167 | 15754 | 20 | 0.067833 | 0.075375 | 0.082917 | 0.090458 | 0.098 |  | 100 | 0.04962 | 0.055821 | 0.062021 | 0.068222 | 0.074422 |  | 50 | 1992.6667 | 5033.5833 | 8074.5 | 11115.4167 | 14156.3333
| 30 | 0.067333 | 0.07475 | 0.082167 | 0.089583 | 0.097 |  | 110 | 0.074513 | 0.083575 | 0.092638 | 0.1017 | 0.11076 |  | 60 | 2442.8333 | 6172 | 9901.1667 | 13630.3333 | 17359.5 | [6 empty] | 30 | 0.11933 | 0.13125 | 0.14317 | 0.15508 | 0.167 |  | 110 |  | 0.141 |  | 0.1545 |  | 0.168 |  | 0.1815 |  | 0.195 |  |  |  | 60 | 1298.6667 | 3350.7917 | 5402.9167 | 7455.0417 | 9507.1667 | 30 | 0.076 | 0.08425 | 0.0925 | 0.10075 | 0.109 |  | 110 | 0.0875 | 0.098 | 0.1085 | 0.119 | 0.1295 |  | 60 | 2552.3333 | 6453.8333 | 10355.3333 | 14256.8333 | 18158.3333 | 30 | 0.067333 | 0.07475 | 0.082167 | 0.089583 | 0.097 |  | 110 | 0.074513 | 0.083575 | 0.092638 | 0.1017 | 0.11076 |  | 60 | 2442.8333 | 6172 | 9901.1667 | 13630.3333 | 17359.5 | 30 | 0.058667 | 0.06525 | 0.071833 | 0.078417 | 0.085 |  | 110 | 0.061525 | 0.069151 | 0.076776 | 0.084402 | 0.092027 |  | 60 | 2333.3333 | 5890.1667 | 9447 | 13003.8333 | 16560.6667
| 40 | 0.05675 | 0.063062 | 0.069375 | 0.075687 | 0.082 |  | 120 | 0.089015 | 0.099766 | 0.11052 | 0.12127 | 0.13202 |  | 70 | 2674 | 6746.75 | 10819.5 | 14892.25 | 18965 | [6 empty] | 40 | 0.1015 | 0.11163 | 0.12175 | 0.13187 | 0.142 |  | 120 |  | 0.1678 |  | 0.18385 |  | 0.1999 |  | 0.21595 |  | 0.232 |  |  |  | 70 | 1486 | 3833.75 | 6181.5 | 8529.25 | 10877 | 40 | 0.064 | 0.071 | 0.078 | 0.085 | 0.092 |  | 120 | 0.1046 | 0.11705 | 0.1295 | 0.14195 | 0.1544 |  | 70 | 2674 | 6746.75 | 10819.5 | 14892.25 | 18965 | 40 | 0.05675 | 0.063062 | 0.069375 | 0.075687 | 0.082 |  | 120 | 0.089015 | 0.099766 | 0.11052 | 0.12127 | 0.13202 |  | 70 | 2674 | 6746.75 | 10819.5 | 14892.25 | 18965 | 40 | 0.0495 | 0.055125 | 0.06075 | 0.066375 | 0.072 |  | 120 | 0.073431 | 0.082481 | 0.091532 | 0.10058 | 0.10963 |  | 70 | 2674 | 6746.75 | 10819.5 | 14892.25 | 18965
| 50 | 0.046167 | 0.051375 | 0.056583 | 0.061792 | 0.067 |  | 130 | 0.10352 | 0.11596 | 0.12839 | 0.14083 | 0.15327 | [13 empty] | 50 | 0.083667 | 0.092 | 0.10033 | 0.10867 | 0.117 |  | 130 |  | 0.1946 |  | 0.2132 |  | 0.2318 |  | 0.2504 |  | 0.269 |  |  |  | BLG = (9.854E-03 x Amb + 9.279E-02) x Floor Area - 1.083E+01 x Amb - 1.037E+02 | [5 empty] | 50 | 0.052 | 0.05775 | 0.0635 | 0.06925 | 0.075 |  | 130 | 0.1217 | 0.1361 | 0.1505 | 0.1649 | 0.1793 |  | BLG = (5.708E-03 x Amb + 9.580E-01) x Floor Area - 4.9583E+00 x Amb - 1.052E+03 | [5 empty] | 50 | 0.046167 | 0.051375 | 0.056583 | 0.061792 | 0.067 |  | 130 | 0.10352 | 0.11596 | 0.12839 | 0.14083 | 0.15327 |  | BLG = (ALF 1.0 Value + ALF 2.0 Value) / 2 | [5 empty] | 50 | 0.040333 | 0.045 | 0.049667 | 0.054333 | 0.059 |  | 130 | 0.085336 | 0.095811 | 0.10629 | 0.11676 | 0.12724 |  | BLG = (1.720E-02 x Amb + 1.538E-01) x Floor Area - 1.753E+01 x Amb - 1.720E+02
| 60 | 0.035583 | 0.039688 | 0.043792 | 0.047896 | 0.052 |  | 140 | 0.11802 | 0.13215 | 0.14627 | 0.1604 | 0.17452 | [13 empty] | 60 | 0.065833 | 0.072375 | 0.078917 | 0.085458 | 0.092 |  | 140 |  | 0.2214 |  | 0.24255 |  | 0.2637 |  | 0.28485 |  | 0.306 | [9 empty] | 60 | 0.04 | 0.0445 | 0.049 | 0.0535 | 0.058 |  | 140 | 0.1388 | 0.15515 | 0.1715 | 0.18785 | 0.2042 | [7 empty] | 60 | 0.035583 | 0.039688 | 0.043792 | 0.047896 | 0.052 |  | 140 | 0.11802 | 0.13215 | 0.14627 | 0.1604 | 0.17452 | [7 empty] | 60 | 0.031167 | 0.034875 | 0.038583 | 0.042292 | 0.046 |  | 140 | 0.097241 | 0.10914 | 0.12104 | 0.13294 | 0.14484
| 70 | 0.025 | 0.028 | 0.031 | 0.034 | 0.037 |  | 150 | 0.13252 | 0.14834 | 0.16415 | 0.17996 | 0.19577 |  | Leakage Correction (LCF) for Latent Gain | [11 empty] | 70 | 0.048 | 0.05275 | 0.0575 | 0.06225 | 0.067 |  | 150 |  | 0.2482 |  | 0.2719 |  | 0.2956 |  | 0.3193 |  | 0.343 |  |  |  | Leakage Correction (LCF) for Latent Gain | [5 empty] | 70 | 0.028 | 0.03125 | 0.0345 | 0.03775 | 0.041 |  | 150 | 0.1559 | 0.1742 | 0.1925 | 0.2108 | 0.2291 |  | Leakage Correction (LCF) for Latent Gain | [5 empty] | 70 | 0.025 | 0.028 | 0.031 | 0.034 | 0.037 |  | 150 | 0.13252 | 0.14834 | 0.16415 | 0.17996 | 0.19577 |  | Leakage Correction (LCF) for Latent Gain | [5 empty] | 70 | 0.022 | 0.02475 | 0.0275 | 0.03025 | 0.033 |  | 150 | 0.10915 | 0.12247 | 0.1358 | 0.14912 | 0.16245 |  | Leakage Correction (LCF) for Latent Gain
[8 empty] | 160 | 0.14703 | 0.16453 | 0.18203 | 0.19953 | 0.21703 |  | Leakage | Any R-Value | [10 empty] | BHLF = (-5.972E-08 x Amb + 5.764E-06) x Floor Area - 1.604E-03 x Amb + 1.555E-01 | [6 empty] | 160 |  | 0.275 |  | 0.30125 |  | 0.3275 |  | 0.35375 |  | 0.38 |  |  |  | Leakage | Any R-Value |  |  |  |  | BHLF = (-4.167E-08 x Amb + 4.000E-06) x Floor Area - 1.075E-03 x Amb + 1.000E-01 | [6 empty] | 160 | 0.173 | 0.19325 | 0.2135 | 0.23375 | 0.254 |  | Leakage | Any R-Value |  |  |  |  | BHLF = (ALF 1.0 Value + ALF 2.0 Value) / 2 | [6 empty] | 160 | 0.14703 | 0.16453 | 0.18203 | 0.19953 | 0.21703 |  | Leakage | Any R-Value |  |  |  |  | BHLF = (-3.194-08 x Amb + 3.153E-06) x Floor Area - 8.208E-04 x Amb + 7.671E-02 | [6 empty] | 160 | 0.12105 | 0.1358 | 0.15055 | 0.1653 | 0.18006 |  | Leakage | Any R-Value
[15 empty] | 0.06 / 0.06 |  |  | 0.29455 | [15 empty] | BSGF = (8.500E-08 x Amb - 4.850E-06) x Floor Area + 2.425E-03 x Amb - 1.393E-01 | [13 empty] | 0.06 / 0.06 |  |  | 0.29899 | [9 empty] | BSGF = (6.500E-08 x Amb - 3.650E-06) x Floor Area + 1.515E-03 x Amb - 8.965E-02 | [6 empty] | 0.06 / 0.06 |  |  | 0.29378 | [9 empty] | BSGF = (ALF 1.0 Value + ALF 2.0 Value) / 2 | [6 empty] | 0.06 / 0.06 |  |  | 0.29455 | [9 empty] | BSGF = (4.75E-08 x Amb - 2.684E-06) x Floor Area + 1.048E-03 x Amb - 6.138E-02 | [6 empty] | 0.06 / 0.06 |  |  | 0.29533
| R-Value Correction |  | R2 | R4 | R6 | R8 | [8 empty] | 0.09 / 0.15 |  |  | 0.64364 | [8 empty] | R-Value Correction |  | R2 | R4 | R6 | R8 | [15 empty] | 0.09 / 0.15 |  |  | 0.64735 |  |  | R-Value Correction |  | R2 | R4 | R6 | R8 | [8 empty] | 0.09 / 0.15 |  |  | 0.64391 |  |  | R-Value Correction |  | R2 | R4 | R6 | R8 | [8 empty] | 0.09 / 0.15 |  |  | 0.64364 |  |  | R-Value Correction |  | R2 | R4 | R6 | R8 | [8 empty] | 0.09 / 0.15 |  |  | 0.64336
|  |  | 1.8384 | 1.2455 | 1 | 0.86104 |  | R-Value Correction |  | R2 | R4 | R6 | R8 |  | 0.12 / 0.24 |  |  | 1 | [8 empty] | (WIF - Heat Loss) |  | 1.7478 | 1.2261 | 1 | 0.86957 |  | R-Value Correction |  |  |  | R2 |  | R4 |  | R6 |  | R8 |  |  |  | 0.12 / 0.24 |  |  | 1 |  |  | (WIF - Heat Loss) |  | 1.8434 | 1.241 | 1 | 0.85542 |  | R-Value Correction |  | R2 | R4 | R6 | R8 |  | 0.12 / 0.24 |  |  | 1 |  |  | (WIF - Heat Loss) |  | 1.8384 | 1.2455 | 1 | 0.86104 |  | R-Value Correction |  | R2 | R4 | R6 | R8 |  | 0.12 / 0.24 |  |  | 1 |  |  | (WIF - Heat Loss) |  | 1.8333 | 1.25 | 1 | 0.86667 |  | R-Value Correction |  | R2 | R4 | R6 | R8 |  | 0.12 / 0.24 |  |  | 1
[10 empty] | 1.9045 | 1.2571 | 1 | 0.8598 |  | 0.24 / 0.47 |  |  | 2.1486 | [15 empty] | (WIF - Sensible Gain) |  |  |  | 1.8247 |  | 1.2727 |  | 1 |  | 0.85065 |  |  |  | 0.24 / 0.47 |  |  | 2.0251 | [9 empty] | (WIF - Sensible Gain) |  | 1.934 | 1.2642 | 1 | 0.85849 |  | 0.24 / 0.47 |  |  | 2.0223 | [9 empty] | (WIF - Sensible Gain) |  | 1.9045 | 1.2571 | 1 | 0.8598 |  | 0.24 / 0.47 |  |  | 2.1486 | [9 empty] | (WIF - Sensible Gain) |  | 1.875 | 1.25 | 1 | 0.86111 |  | 0.24 / 0.47 |  |  | 2.2748
[15 empty] | 0.35 / 0.70 |  |  | 3.1191 | [29 empty] | 0.35 / 0.70 |  |  | 3.0684 | [16 empty] | 0.35 / 0.70 |  |  | 3.0632 | [16 empty] | 0.35 / 0.70 |  |  | 3.1191 | [16 empty] | 0.35 / 0.70 |  |  | 3.1749
| Leakage Correction (LCF) for Heat Loss | [6 empty] | Leakage Correction (LCF) for Sensible Gain | [18 empty] | Leakage Correction (LCF) for Heat Loss | [6 empty] | Leakage Correction (LCF) for Sensible Gain | [13 empty] | Surface Area Adjustment (LGA) for Latent Gain | [5 empty] | Leakage Correction (LCF) for Heat Loss | [6 empty] | Leakage Correction (LCF) for Sensible Gain | [6 empty] | Surface Area Adjustment (LGA) for Latent Gain | [5 empty] | Leakage Correction (LCF) for Heat Loss | [6 empty] | Leakage Correction (LCF) for Sensible Gain | [6 empty] | Surface Area Adjustment (LGA) for Latent Gain | [5 empty] | Leakage Correction (LCF) for Heat Loss | [6 empty] | Leakage Correction (LCF) for Sensible Gain | [6 empty] | Surface Area Adjustment (LGA) for Latent Gain
| Leakage | R2 | R4 | R6 | R8 |  |  | Leakage | R2 | R4 | R6 | R8 | [14 empty] | Leakage | R2 | R4 | R6 | R8 |  |  | Leakage |  | R2 |  | R4 |  | R6 |  | R8 | [5 empty] | Return side LGA = Actual return-side area / Default return-side area | [5 empty] | Leakage | R2 | R4 | R6 | R8 |  |  | Leakage | R2 | R4 | R6 | R8 |  |  | Return side LGA = Actual return-side area / Default return-side area | [5 empty] | Leakage | R2 | R4 | R6 | R8 |  |  | Leakage | R2 | R4 | R6 | R8 |  |  | Return side LGA = Actual return-side area / Default return-side area | [5 empty] | Leakage | R2 | R4 | R6 | R8 |  |  | Leakage | R2 | R4 | R6 | R8 |  |  | Return side LGA = Actual return-side area / Default return-side area
| 0.06 / 0.06 | 0.85039 | 0.78061 | 0.72548 | 0.68543 |  |  | 0.06 / 0.06 | 0.77058 | 0.77324 | 0.73409 | 0.69582 | [14 empty] | 0.06 / 0.06 | 0.85544 | 0.77791 | 0.73408 | 0.68809 |  |  | 0.06 / 0.06 |  | 0.85543 |  | 0.78613 |  | 0.73763 |  | 0.70474 | [11 empty] | 0.06 / 0.06 | 0.85737 | 0.77952 | 0.72415 | 0.68506 |  |  | 0.06 / 0.06 | 0.84419 | 0.77528 | 0.73038 | 0.68875 | [8 empty] | 0.06 / 0.06 | 0.85039 | 0.78061 | 0.72548 | 0.68543 |  |  | 0.06 / 0.06 | 0.77058 | 0.77324 | 0.73409 | 0.69582 | [8 empty] | 0.06 / 0.06 | 0.84341 | 0.78169 | 0.7268 | 0.6858 |  |  | 0.06 / 0.06 | 0.68378 | 0.77119 | 0.73781 | 0.70289
| 0.09 / 0.15 | 0.92703 | 0.88814 | 0.86138 | 0.84394 |  |  | 0.09 / 0.15 | 0.92343 | 0.88736 | 0.86238 | 0.84168 | [14 empty] | 0.09 / 0.15 | 0.92746 | 0.88819 | 0.8633 | 0.84331 |  |  | 0.09 / 0.15 |  | 0.93196 |  | 0.89553 |  | 0.86782 |  | 0.8525 | [5 empty] | Procedure for Latent Gain Adjustment | [5 empty] | 0.09 / 0.15 | 0.93526 | 0.88717 | 0.86153 | 0.84451 |  |  | 0.09 / 0.15 | 0.92458 | 0.88961 | 0.86695 | 0.84135 |  |  | Procedure for Latent Gain Adjustment | [5 empty] | 0.09 / 0.15 | 0.92703 | 0.88814 | 0.86138 | 0.84394 |  |  | 0.09 / 0.15 | 0.92343 | 0.88736 | 0.86238 | 0.84168 |  |  | Procedure for Latent Gain Adjustment | [5 empty] | 0.09 / 0.15 | 0.91881 | 0.88911 | 0.86124 | 0.84337 |  |  | 0.09 / 0.15 | 0.92227 | 0.8851 | 0.8578 | 0.84202 |  |  | Procedure for Latent Gain Adjustment
| 0.12 / 0.24 | 1 | 1 | 1 | 1 |  |  | 0.12 / 0.24 | 1 | 1 | 1 | 1 | [14 empty] | 0.12 / 0.24 | 1 | 1 | 1 | 1 |  |  | 0.12 / 0.24 |  | 1 |  | 1 |  | 1 |  | 1 | [5 empty] | Step 1: Select the base case latent gain value (multiply by - 1.0 for negative Grains). | [5 empty] | 0.12 / 0.24 | 1 | 1 | 1 | 1 |  |  | 0.12 / 0.24 | 1 | 1 | 1 | 1 |  |  | Step 1: Select the base case latent gain value (multiply by - 1.0 for negative Grains). | [5 empty] | 0.12 / 0.24 | 1 | 1 | 1 | 1 |  |  | 0.12 / 0.24 | 1 | 1 | 1 | 1 |  |  | Step 1: Select the base case latent gain factor. | [5 empty] | 0.12 / 0.24 | 1 | 1 | 1 | 1 |  |  | 0.12 / 0.24 | 1 | 1 | 1 | 1 |  |  | Step 1: Select the base case latent gain value (multiply by - 1.0 for negative Grains).
| 0.24 / 0.47 | 1.2382 | 1.3414 | 1.3998 | 1.4671 |  |  | 0.24 / 0.47 | 1.2897 | 1.4113 | 1.4898 | 1.5602 | [14 empty] | 0.24 / 0.47 | 1.2214 | 1.3111 | 1.3972 | 1.4535 |  |  | 0.24 / 0.47 |  | 1.2711 |  | 1.3793 |  | 1.4689 |  | 1.5382 | [5 empty] | Step 2: Apply leakage correction to the Step 1 value. | [5 empty] | 0.24 / 0.47 | 1.2415 | 1.3437 | 1.389 | 1.4598 |  |  | 0.24 / 0.47 | 1.2663 | 1.4044 | 1.4831 | 1.5611 |  |  | Step 2: Apply leakage correction to the Step 1 value. | [5 empty] | 0.24 / 0.47 | 1.2382 | 1.3414 | 1.3998 | 1.4671 |  |  | 0.24 / 0.47 | 1.2897 | 1.4113 | 1.4898 | 1.5602 |  |  | Step 2: Apply leakage correction to the Step 1 value. | [5 empty] | 0.24 / 0.47 | 1.235 | 1.3392 | 1.4106 | 1.4743 |  |  | 0.24 / 0.47 | 1.3131 | 1.4183 | 1.4966 | 1.5594 |  |  | Step 2: Apply leakage correction to the Step 1 value.
| 0.35 / 0.70 | 1.4816 | 1.6849 | 1.8167 | 1.9487 |  |  | 0.35 / 0.70 | 1.5828 | 1.8203 | 1.9792 | 2.1209 | [14 empty] | 0.35 / 0.70 | 1.4351 | 1.6217 | 1.7821 | 1.9036 |  |  | 0.35 / 0.70 |  | 1.5493 |  | 1.7568 |  | 1.9219 |  | 2.0656 | [5 empty] | Step 3: Apply surface area adjustment to the Step 2 value. | [5 empty] | 0.35 / 0.70 | 1.4877 | 1.6915 | 1.8049 | 1.9396 |  |  | 0.35 / 0.70 | 1.5266 | 1.7736 | 1.9421 | 2.1012 |  |  | Step 3: Apply surface area adjustment to the Step 2 value. | [5 empty] | 0.35 / 0.70 | 1.4816 | 1.6849 | 1.8167 | 1.9487 |  |  | 0.35 / 0.70 | 1.5828 | 1.8203 | 1.9792 | 2.1209 |  |  | Step 3: Apply surface area adjustment to the Step 2 value. | [5 empty] | 0.35 / 0.70 | 1.4755 | 1.6784 | 1.8286 | 1.9579 |  |  | 0.35 / 0.70 | 1.6391 | 1.867 | 2.0164 | 2.1406 |  |  | Step 3: Apply surface area adjustment to the Step 2 value.
| Default Duct Wall Surface Area (SqFt) | [9 empty] | Surface Area Factors | [15 empty] | Default Duct Wall Surface Area (SqFt) | [12 empty] | Surface Area Factors | [13 empty] | Default Duct Wall Surface Area (SqFt) | [9 empty] | Surface Area Factors | [9 empty] | Default Duct Wall Surface Area (SqFt) | [9 empty] | Surface Area Factors | [9 empty] | Default Duct Wall Surface Area (SqFt) | [9 empty] | Surface Area Factors
[11 empty] | Leakage | Ks | Kr | [26 empty] | Leakage |  | Ks |  | Kr | [19 empty] | Leakage | Ks | Kr | [17 empty] | Leakage | Ks | Kr | [17 empty] | Leakage | Ks | Kr
| Floor Area Look-Up Value | [9 empty] | 0.06 / 0.06 | 0.71857 | 0.28143 | [13 empty] | Floor Area Look-Up Value | [12 empty] | 0.06 / 0.06 |  | 0.72581 |  | 0.27419 | [9 empty] | Floor Area Look-Up Value | [9 empty] | 0.06 / 0.06 | 0.71827 | 0.28173 | [7 empty] | Floor Area Look-Up Value | [9 empty] | 0.06 / 0.06 | 0.71857 | 0.28143 | [7 empty] | Floor Area Look-Up Value | [9 empty] | 0.06 / 0.06 | 0.71888 | 0.28112
| 3000 | 3000 | 6000 | 6000 | 9000 | 9000 | 12000 | 12000 | 15000 | 15000 | 0.09 / 0.15 | 0.69169 | 0.30831 | [13 empty] | 3,000 SqFt |  | 6,000 SqFt |  | 9,000 SqFt |  | 12,000 SqFt |  |  | 15,000 SqFt |  |  |  | 0.09 / 0.15 |  | 0.69943 |  | 0.30057 | [9 empty] | 3,000 SqFt |  | 6,000 SqFt |  | 9,000 SqFt |  | 12,000 SqFt |  | 15,000 SqFt |  | 0.09 / 0.15 | 0.69134 | 0.30866 | [7 empty] | 3,000 SqFt |  | 6,000 SqFt |  | 9,000 SqFt |  | 12,000 SqFt |  | 15,000 SqFt |  | 0.09 / 0.15 | 0.69169 | 0.30831 | [7 empty] | 3,000 SqFt |  | 6,000 SqFt |  | 9,000 SqFt |  | 12,000 SqFt |  | 15,000 SqFt |  | 0.09 / 0.15 | 0.69204 | 0.30796
| Supply | Return | Supply | Return | Supply | Return | Supply | Return | Supply | Return | 0.12 / 0.24 | 0.66891 | 0.33109 | [13 empty] | Supply | Return | Supply | Return | Supply | Return | Supply | Return |  | Supply |  | Return |  | 0.12 / 0.24 |  | 0.67707 |  | 0.32293 | [9 empty] | Supply | Return | Supply | Return | Supply | Return | Supply | Return | Supply | Return | 0.12 / 0.24 | 0.66853 | 0.33147 | [7 empty] | Supply | Return | Supply | Return | Supply | Return | Supply | Return | Supply | Return | 0.12 / 0.24 | 0.66891 | 0.33109 | [7 empty] | Supply | Return | Supply | Return | Supply | Return | Supply | Return | Supply | Return | 0.12 / 0.24 | 0.66929 | 0.33071
| 490.5 | 205 | 1127.5 | 434 | 1897.5 | 730 | 2764 | 1042 | 3594 | 1413.5 | 0.24 / 0.47 | 0.64564 | 0.35436 | [13 empty] | 326 | 121 | 711 | 254 | 1085 | 428 | 1509 | 610 |  | 2284 |  | 829 |  | 0.24 / 0.47 |  | 0.65407 |  | 0.34593 | [9 empty] | 393 | 170 | 949 | 359 | 1625 | 605 | 2262 | 863 | 2941 | 1171 | 0.24 / 0.47 | 0.64529 | 0.35471 | [7 empty] | 490.5 | 205 | 1127.5 | 434 | 1897.5 | 730 | 2764 | 1042 | 3594 | 1413.5 | 0.24 / 0.47 | 0.64564 | 0.35436 | [7 empty] | 588 | 240 | 1306 | 509 | 2170 | 855 | 3266 | 1221 | 4247 | 1656 | 0.24 / 0.47 | 0.646 | 0.354
[11 empty] | 0.35 / 0.70 | 0.63471 | 0.36529 | [13 empty] | See Section 9-9 for instruction for determining the floor area look-up value. | [12 empty] | 0.35 / 0.70 |  | 0.63611 |  | 0.36389 | [9 empty] | See Section 9-9 for instruction for determining the floor area look-up value. | [9 empty] | 0.35 / 0.70 | 0.6416 | 0.3584 | [7 empty] | See Section 9-9 for instruction for determining the floor area look-up value. | [9 empty] | 0.35 / 0.70 | 0.63471 | 0.36529 | [7 empty] | See Section 9-9 for instruction for determining the floor area look-up value. | [9 empty] | 0.35 / 0.70 | 0.62782 | 0.37218
[27 empty] | ALF | Radial or Spider Supply and Return System Installed in a Unconditioned Space or Outdoors | [23 empty] | Table |  | ALF | Radial or Spider Supply and Return System Installed in a Unconditioned Space or Outdoors | [16 empty] | Table |  | ALF | Radial or Spider Supply and Return System Installed in a Unconditioned Space or Outdoors | [16 empty] | Table |  | ALF | Radial or Spider Supply and Return System Installed in a Unconditioned Space or Outdoors | [16 empty] | Table
[27 empty] | 0.5 | Supply location = Perimeter of floor plan |  |  |  | Number of supplies: 3,000 SF = 15; 6,000 SF = 20; 9,000 SF = 25; 12,000 SF = 30; 15,000 SF = 35 | [13 empty] | One return for four supplies; returns close to air handler | [5 empty] | 7RP-0.5 |  | 1.0 | Supply location = Perimeter of floor plan |  |  |  | Number of supplies: 3,000 SF = 15; 6,000 SF = 20; 9,000 SF = 25; 12,000 SF = 30; 15,000 SF = 35 | [7 empty] | One return for four supplies; returns close to air handler |  |  |  |  | 7RP-1.0 |  | 1.5 | Supply location = Perimeter of floor plan |  |  |  | Number of supplies: 3,000 SF = 15; 6,000 SF = 20; 9,000 SF = 25; 12,000 SF = 30; 15,000 SF = 35 | [7 empty] | One return for four supplies; returns close to air handler |  |  |  |  | 7RP-1.5 |  | 2.0 | Supply location = Perimter of floor plan |  |  |  | Number of supplies: 3,000 SF = 15; 6,000 SF = 20; 9,000 SF = 25; 12,000 SF = 30; 15,000 SF = 35 | [7 empty] | One return for four supplies; returns close to air handler |  |  |  |  | 7RP-2.0
[28 empty] | Duct leakage Cfm per SqFt of duct surface area (supply / return) = 0.06/0.06; 0.09/0.15; 0.12/0.24; 0.24/0.47; 0.35/0.70 | [17 empty] | Duct wall insulation R-value = 2, 4, 6 and 8 | [8 empty] | Duct leakage Cfm per SqFt of duct surface area (supply / return) = 0.06/0.06; 0.09/0.15; 0.12/0.24; 0.24/0.47; 0.35/0.70 | [11 empty] | Duct wall insulation R-value = 2, 4, 6 and 8 | [7 empty] | Duct leakage Cfm per SqFt of duct surface area (supply / return) = 0.06/0.06; 0.09/0.15; 0.12/0.24; 0.24/0.47; 0.35/0.70 | [11 empty] | Duct wall insulation R-value = 2, 4, 6 and 8 | [7 empty] | Duct leakage Cfm per SqFt of duct surface area (supply / return) = 0.06/0.06; 0.09/0.15; 0.12/0.24; 0.24/0.47; 0.35/0.70 | [11 empty] | Duct wall insulation R-value = 2, 4, 6 and 8
[27 empty] | Base Case Heat Loss Factor (BHLF) | [6 empty] | Base Case Sensible Gain Factor (BSGF) | [13 empty] | ± Btuh Values for Base Case Latent Gain (BLG) | [5 empty] | Base Case Heat Loss Factor (BHLF) | [6 empty] | Base Case Sensible Gain Factor (BSGF) | [6 empty] | ± Btuh Values for Base Case Latent Gain (BLG) | [5 empty] | Base Case Heat Loss Factor (BHLF) | [6 empty] | Base Case Sensible Gain Factor (BSGF) | [6 empty] | Base Case Latent Gain (BLG) | [5 empty] | Base Case Heat Loss Factor (BHLF) | [6 empty] | Base Case Sensible Gain Factor (BSGF) | [6 empty] | ± Btuh Values for Base Case Latent Gain (BLG)
3 | 7RP-1.5 | Radial or Spider Supply and Return System Installed in a Unconditioned Space or Outdoors, Perimeter Supply Outlets | [24 empty] | R6 Insulation, ASHRAE Sealed (Supply = 0.12, Return = 0.24) | [6 empty] | R6 Insulation, ASHRAE Sealed (Supply = 0.12, Return = 0.24) | [13 empty] | R6 Insulation, ASHRAE Sealed (Supply = 0.12, Return = 0.24) | [5 empty] | R6 Insulation, ASHRAE Sealed (Supply = 0.12, Return = 0.24) | [6 empty] | R6 Insulation, ASHRAE Sealed (Supply = 0.12, Return = 0.24) | [6 empty] | R6 Insulation, ASHRAE Sealed (Supply = 0.12, Return = 0.24) | [5 empty] | R6 Insulation, ASHRAE Sealed (Supply = 0.12, Return = 0.24) | [6 empty] | R6 Insulation, ASHRAE Sealed (Supply = 0.12, Return = 0.24) | [6 empty] | R6 Insulation, ASHRAE Sealed (Supply = 0.12, Return = 0.24) | [5 empty] | R6 Insulation, ASHRAE Sealed (Supply = 0.12, Return = 0.24) | [6 empty] | R6 Insulation, ASHRAE Sealed (Supply = 0.12, Return = 0.24) | [6 empty] | R6 Insulation, ASHRAE Sealed (Supply = 0.12, Return = 0.24)
| Ambient | Square Feet of Floor Area | [5 empty] | Ambient | Square Feet of Floor Area | [5 empty] | Ambient | Square Feet of Floor Area | [10 empty] | Ambient | Square Feet of Floor Area | [5 empty] | Ambient |  | Square Feet of Floor Area | [11 empty] | Ambient | Square Feet of Floor Area |  |  |  |  | Ambient | Square Feet of Floor Area | [5 empty] | Ambient | Square Feet of Floor Area | [5 empty] | Ambient | Square Feet of Floor Area |  |  |  |  | Ambient | Square Feet of Floor Area | [5 empty] | Ambient | Square Feet of Floor Area | [5 empty] | Ambient | Square Feet of Floor Area |  |  |  |  | Ambient | Square Feet of Floor Area | [5 empty] | Ambient | Square Feet of Floor Area | [5 empty] | Ambient | Square Feet of Floor Area
| Dry Bulb | 3000 | 6000 | 9000 | 12000 | 15000 |  | Dry Bulb | 3000 | 6000 | 9000 | 12000 | 15000 |  | Grains | 3000 | 6000 | 9000 | 12000 | 15000 | [6 empty] | Dry Bulb | 3000 | 6000 | 9000 | 12000 | 15000 |  | Dry Bulb |  | 3000 |  | 6000 |  | 9000 |  | 12000 |  | 15000 |  |  |  | ∆ Grains ± | 3000 | 6000 | 9000 | 12000 | 15000 | Dry Bulb | 3000 | 6000 | 9000 | 12000 | 15000 |  | Dry Bulb | 3000 | 6000 | 9000 | 12000 | 15000 |  | ∆ Grains ± | 3000 | 6000 | 9000 | 12000 | 15000 | Dry Bulb | 3000 | 6000 | 9000 | 12000 | 15000 |  | Dry Bulb | 3000 | 6000 | 9000 | 12000 | 15000 |  | Grains | 3000 | 6000 | 9000 | 12000 | 15000 | Dry Bulb | 3000 | 6000 | 9000 | 12000 | 15000 |  | Dry Bulb | 3000 | 6000 | 9000 | 12000 | 15000 |  | ∆ Grains ± | 3000 | 6000 | 9000 | 12000 | 15000
| -20 | 0.177 | 0.19919 | 0.22137 | 0.24356 | 0.26575 |  | 60 | 0.015 | 0.0195 | 0.024 | 0.0285 | 0.033 |  | 10 | 814 | 2169 | 3524 | 4879 | 6234 | [6 empty] | -20 | 0.3255 | 0.35712 | 0.38875 | 0.42037 | 0.452 |  | 60 |  | 0.03 |  | 0.037 |  | 0.044 |  | 0.051 |  | 0.058 |  |  |  | 10 | 566 | 1427.5 | 2289 | 3150.5 | 4012 | -20 | 0.2045 | 0.23 | 0.2555 | 0.281 | 0.3065 |  | 60 | 0.016 | 0.02125 | 0.0265 | 0.03175 | 0.037 |  | 10 | 675 | 1808.25 | 2941.5 | 4074.75 | 5208 | -20 | 0.177 | 0.19919 | 0.22137 | 0.24356 | 0.26575 |  | 60 | 0.015 | 0.0195 | 0.024 | 0.0285 | 0.033 |  | 10 | 814 | 2169 | 3524 | 4879 | 6234 | -20 | 0.1495 | 0.16837 | 0.18725 | 0.20612 | 0.225 |  | 60 | 0.014 | 0.01775 | 0.0215 | 0.02525 | 0.029 |  | 10 | 953 | 2529.75 | 4106.5 | 5683.25 | 7260
| -10 | 0.1625 | 0.18304 | 0.20358 | 0.22412 | 0.24467 |  | 70 | 0.0365 | 0.043462 | 0.050425 | 0.057387 | 0.06435 |  | 20 | 1127.9167 | 2979.6667 | 4831.4167 | 6683.1667 | 8534.9167 | [6 empty] | -10 | 0.29967 | 0.32883 | 0.358 | 0.38717 | 0.41633 |  | 70 |  | 0.0687 |  | 0.07945 |  | 0.0902 |  | 0.10095 |  | 0.1117 |  |  |  | 20 | 770.6667 | 1938.0417 | 3105.4167 | 4272.7917 | 5440.1667 | -10 | 0.18767 | 0.21125 | 0.23483 | 0.25842 | 0.282 |  | 70 | 0.0409 | 0.049 | 0.0571 | 0.0652 | 0.0733 |  | 20 | 941 | 2493.7083 | 4046.4167 | 5599.125 | 7151.8333 | -10 | 0.1625 | 0.18304 | 0.20358 | 0.22412 | 0.24467 |  | 70 | 0.0365 | 0.043462 | 0.050425 | 0.057387 | 0.06435 |  | 20 | 1127.9167 | 2979.6667 | 4831.4167 | 6683.1667 | 8534.9167 | -10 | 0.13733 | 0.15483 | 0.17233 | 0.18983 | 0.20733 |  | 70 | 0.0321 | 0.037925 | 0.04375 | 0.049575 | 0.0554 |  | 20 | 1314.8333 | 3465.625 | 5616.4167 | 7767.2083 | 9918
| 0 | 0.148 | 0.1669 | 0.18579 | 0.20469 | 0.22358 |  | 80 | 0.058 | 0.067425 | 0.07685 | 0.086275 | 0.0957 |  | 30 | 1441.8333 | 3790.3333 | 6138.8333 | 8487.3333 | 10835.8333 | [6 empty] | 0 | 0.27383 | 0.30054 | 0.32725 | 0.35396 | 0.38067 |  | 80 |  | 0.1074 |  | 0.1219 |  | 0.1364 |  | 0.1509 |  | 0.1654 |  |  |  | 30 | 975.3333 | 2448.5833 | 3921.8333 | 5395.0833 | 6868.3333 | 0 | 0.17083 | 0.1925 | 0.21417 | 0.23583 | 0.2575 |  | 80 | 0.0658 | 0.07675 | 0.0877 | 0.09865 | 0.1096 |  | 30 | 1207 | 3179.1667 | 5151.3333 | 7123.5 | 9095.6667 | 0 | 0.148 | 0.1669 | 0.18579 | 0.20469 | 0.22358 |  | 80 | 0.058 | 0.067425 | 0.07685 | 0.086275 | 0.0957 |  | 30 | 1441.8333 | 3790.3333 | 6138.8333 | 8487.3333 | 10835.8333 | 0 | 0.12517 | 0.14129 | 0.15742 | 0.17354 | 0.18967 |  | 80 | 0.0502 | 0.0581 | 0.066 | 0.0739 | 0.0818 |  | 30 | 1676.6667 | 4401.5 | 7126.3333 | 9851.1667 | 12576
| 10 | 0.1335 | 0.15075 | 0.168 | 0.18525 | 0.2025 |  | 90 | 0.0795 | 0.091388 | 0.10328 | 0.11516 | 0.12705 |  | 40 | 1755.75 | 4601 | 7446.25 | 10291.5 | 13136.75 | [6 empty] | 10 | 0.248 | 0.27225 | 0.2965 | 0.32075 | 0.345 |  | 90 |  | 0.1461 |  | 0.16435 |  | 0.1826 |  | 0.20085 |  | 0.2191 |  |  |  | 40 | 1180 | 2959.125 | 4738.25 | 6517.375 | 8296.5 | 10 | 0.154 | 0.17375 | 0.1935 | 0.21325 | 0.233 |  | 90 | 0.0907 | 0.1045 | 0.1183 | 0.1321 | 0.1459 |  | 40 | 1473 | 3864.625 | 6256.25 | 8647.875 | 11039.5 | 10 | 0.1335 | 0.15075 | 0.168 | 0.18525 | 0.2025 |  | 90 | 0.0795 | 0.091388 | 0.10328 | 0.11516 | 0.12705 |  | 40 | 1755.75 | 4601 | 7446.25 | 10291.5 | 13136.75 | 10 | 0.113 | 0.12775 | 0.1425 | 0.15725 | 0.172 |  | 90 | 0.0683 | 0.078275 | 0.08825 | 0.098225 | 0.1082 |  | 40 | 2038.5 | 5337.375 | 8636.25 | 11935.125 | 15234
| 20 | 0.119 | 0.1346 | 0.15021 | 0.16581 | 0.18142 |  | 100 | 0.101 | 0.11535 | 0.1297 | 0.14405 | 0.1584 |  | 50 | 2069.6667 | 5411.6667 | 8753.6667 | 12095.6667 | 15437.6667 | [6 empty] | 20 | 0.22217 | 0.24396 | 0.26575 | 0.28754 | 0.30933 |  | 100 |  | 0.1848 |  | 0.2068 |  | 0.2288 |  | 0.2508 |  | 0.2728 |  |  |  | 50 | 1384.6667 | 3469.6667 | 5554.6667 | 7639.6667 | 9724.6667 | 20 | 0.13717 | 0.155 | 0.17283 | 0.19067 | 0.2085 |  | 100 | 0.1156 | 0.13225 | 0.1489 | 0.16555 | 0.1822 |  | 50 | 1739 | 4550.0833 | 7361.1667 | 10172.25 | 12983.3333 | 20 | 0.119 | 0.1346 | 0.15021 | 0.16581 | 0.18142 |  | 100 | 0.101 | 0.11535 | 0.1297 | 0.14405 | 0.1584 |  | 50 | 2069.6667 | 5411.6667 | 8753.6667 | 12095.6667 | 15437.6667 | 20 | 0.10083 | 0.11421 | 0.12758 | 0.14096 | 0.15433 |  | 100 | 0.0864 | 0.09845 | 0.1105 | 0.12255 | 0.1346 |  | 50 | 2400.3333 | 6273.25 | 10146.1667 | 14019.0833 | 17892
| 30 | 0.1045 | 0.11846 | 0.13242 | 0.14637 | 0.16033 |  | 110 | 0.1225 | 0.13931 | 0.15612 | 0.17294 | 0.18975 |  | 60 | 2383.5833 | 6222.3333 | 10061.0833 | 13899.8333 | 17738.5833 | [6 empty] | 30 | 0.19633 | 0.21567 | 0.235 | 0.25433 | 0.27367 |  | 110 |  | 0.2235 |  | 0.24925 |  | 0.275 |  | 0.30075 |  | 0.3265 |  |  |  | 60 | 1589.3333 | 3980.2083 | 6371.0833 | 8761.9583 | 11152.8333 | 30 | 0.12033 | 0.13625 | 0.15217 | 0.16808 | 0.184 |  | 110 | 0.1405 | 0.16 | 0.1795 | 0.199 | 0.2185 |  | 60 | 2005 | 5235.5417 | 8466.0833 | 11696.625 | 14927.1667 | 30 | 0.1045 | 0.11846 | 0.13242 | 0.14637 | 0.16033 |  | 110 | 0.1225 | 0.13931 | 0.15612 | 0.17294 | 0.18975 |  | 60 | 2383.5833 | 6222.3333 | 10061.0833 | 13899.8333 | 17738.5833 | 30 | 0.088667 | 0.10067 | 0.11267 | 0.12467 | 0.13667 |  | 110 | 0.1045 | 0.11862 | 0.13275 | 0.14688 | 0.161 |  | 60 | 2762.1667 | 7209.125 | 11656.0833 | 16103.0417 | 20550
| 40 | 0.09 | 0.10231 | 0.11462 | 0.12694 | 0.13925 |  | 120 | 0.144 | 0.16328 | 0.18255 | 0.20183 | 0.2211 |  | 70 | 2697.5 | 7033 | 11368.5 | 15704 | 20039.5 | [6 empty] | 40 | 0.1705 | 0.18738 | 0.20425 | 0.22112 | 0.238 |  | 120 |  | 0.2622 |  | 0.2917 |  | 0.3212 |  | 0.3507 |  | 0.3802 |  |  |  | 70 | 1794 | 4490.75 | 7187.5 | 9884.25 | 12581 | 40 | 0.1035 | 0.1175 | 0.1315 | 0.1455 | 0.1595 |  | 120 | 0.1654 | 0.18775 | 0.2101 | 0.23245 | 0.2548 |  | 70 | 2271 | 5921 | 9571 | 13221 | 16871 | 40 | 0.09 | 0.10231 | 0.11462 | 0.12694 | 0.13925 |  | 120 | 0.144 | 0.16328 | 0.18255 | 0.20183 | 0.2211 |  | 70 | 2697.5 | 7033 | 11368.5 | 15704 | 20039.5 | 40 | 0.0765 | 0.087125 | 0.09775 | 0.10837 | 0.119 |  | 120 | 0.1226 | 0.1388 | 0.155 | 0.1712 | 0.1874 |  | 70 | 3124 | 8145 | 13166 | 18187 | 23208
| 50 | 0.0755 | 0.086167 | 0.096833 | 0.1075 | 0.11817 |  | 130 | 0.1655 | 0.18724 | 0.20898 | 0.23071 | 0.25245 | [13 empty] | 50 | 0.14467 | 0.15908 | 0.1735 | 0.18792 | 0.20233 |  | 130 |  | 0.3009 |  | 0.33415 |  | 0.3674 |  | 0.40065 |  | 0.4339 |  |  |  | BLG = (1.020E-02 x Amb + 1.852E-01) x Floor Area - 1.012E+01 x Amb - 1.943E+02 | [5 empty] | 50 | 0.086667 | 0.09875 | 0.11083 | 0.12292 | 0.135 |  | 130 | 0.1903 | 0.2155 | 0.2407 | 0.2659 | 0.2911 |  | BLG = (1.398E-02 x Amb + 2.379E-01) x Floor Area - 1.535E+01 x Amb - 3.048E+02 | [5 empty] | 50 | 0.0755 | 0.086167 | 0.096833 | 0.1075 | 0.11817 |  | 130 | 0.1655 | 0.18724 | 0.20898 | 0.23071 | 0.25245 |  | BLG = (ALF 1.0 Value + ALF 2.0 Value) / 2 | [5 empty] | 50 | 0.064333 | 0.073583 | 0.082833 | 0.092083 | 0.10133 |  | 130 | 0.1407 | 0.15898 | 0.17725 | 0.19553 | 0.2138 |  | BLG = (1.913E-02 x Amb + 3.342E-01) x Floor Area - 1.122E+01 x Amb - 4.115E+02
| 60 | 0.061 | 0.070021 | 0.079042 | 0.088062 | 0.097083 |  | 140 | 0.187 | 0.2112 | 0.2354 | 0.2596 | 0.2838 | [13 empty] | 60 | 0.11883 | 0.13079 | 0.14275 | 0.15471 | 0.16667 |  | 140 |  | 0.3396 |  | 0.3766 |  | 0.4136 |  | 0.4506 |  | 0.4876 | [9 empty] | 60 | 0.069833 | 0.08 | 0.090167 | 0.10033 | 0.1105 |  | 140 | 0.2152 | 0.24325 | 0.2713 | 0.29935 | 0.3274 | [7 empty] | 60 | 0.061 | 0.070021 | 0.079042 | 0.088062 | 0.097083 |  | 140 | 0.187 | 0.2112 | 0.2354 | 0.2596 | 0.2838 | [7 empty] | 60 | 0.052167 | 0.060042 | 0.067917 | 0.075792 | 0.083667 |  | 140 | 0.1588 | 0.17915 | 0.1995 | 0.21985 | 0.2402
| 70 | 0.0465 | 0.053875 | 0.06125 | 0.068625 | 0.076 |  | 150 | 0.2085 | 0.23516 | 0.26182 | 0.28849 | 0.31515 |  | Leakage Correction (LCF) for Latent Gain | [11 empty] | 70 | 0.093 | 0.1025 | 0.112 | 0.1215 | 0.131 |  | 150 |  | 0.3783 |  | 0.41905 |  | 0.4598 |  | 0.50055 |  | 0.5413 |  |  |  | Leakage Correction (LCF) for Latent Gain | [5 empty] | 70 | 0.053 | 0.06125 | 0.0695 | 0.07775 | 0.086 |  | 150 | 0.2401 | 0.271 | 0.3019 | 0.3328 | 0.3637 |  | Leakage Correction (LCF) for Latent Gain | [5 empty] | 70 | 0.0465 | 0.053875 | 0.06125 | 0.068625 | 0.076 |  | 150 | 0.2085 | 0.23516 | 0.26182 | 0.28849 | 0.31515 |  | Leakage Correction (LCF) for Latent Gain | [5 empty] | 70 | 0.04 | 0.0465 | 0.053 | 0.0595 | 0.066 |  | 150 | 0.1769 | 0.19933 | 0.22175 | 0.24417 | 0.2666 |  | Leakage Correction (LCF) for Latent Gain
[8 empty] | 160 | 0.23 | 0.25913 | 0.28825 | 0.31738 | 0.3465 |  | Leakage | Any R-Value | [10 empty] | BHLF = (-8.194E-08 x Amb + 8.903E-06) x Floor Area - 2.338E-03 x Amb + 2.471E-01 | [6 empty] | 160 |  | 0.417 |  | 0.4615 |  | 0.506 |  | 0.5505 |  | 0.595 |  |  |  | Leakage | Any R-Value |  |  |  |  | BHLF = (-6.389E-08 x Amb + 7.222E-06) x Floor Area - 1.492E-03 x Amb + 1.492E-01 | [6 empty] | 160 | 0.265 | 0.29875 | 0.3325 | 0.36625 | 0.4 |  | Leakage | Any R-Value |  |  |  |  | BHLF = (ALF 1.0 Value + ALF 2.0 Value) / 2 | [6 empty] | 160 | 0.23 | 0.25913 | 0.28825 | 0.31738 | 0.3465 |  | Leakage | Any R-Value |  |  |  |  | BHLF = (-4.583-08 x Amb + 5.375E-06) x Floor Area - 1.079E-03 x Amb + 1.090E-01 | [6 empty] | 160 | 0.195 | 0.2195 | 0.244 | 0.2685 | 0.293 |  | Leakage | Any R-Value
[15 empty] | 0.06 / 0.06 |  |  | 0.32588 | [15 empty] | BSGF = (1.250E-07 x Amb - 5.167E-06) x Floor Area + 3.495E-03 x Amb - 1.867E-01 | [13 empty] | 0.06 / 0.06 |  |  | 0.32788 | [9 empty] | BSGF = (9.500E-08 x Amb - 3.950E-06) x Floor Area + 2.205E-03 x Amb - 1.216E-01 | [6 empty] | 0.06 / 0.06 |  |  | 0.32444 | [9 empty] | BSGF = (ALF 1.0 Value + ALF 2.0 Value) / 2 | [6 empty] | 0.06 / 0.06 |  |  | 0.32588 | [9 empty] | BSGF = (6.917E-08 x Amb - 2.900E-06) x Floor Area + 1.603E-03 x Amb - 8.590E-02 | [6 empty] | 0.06 / 0.06 |  |  | 0.32733
| R-Value Correction |  | R2 | R4 | R6 | R8 | [8 empty] | 0.09 / 0.15 |  |  | 0.66072 | [8 empty] | R-Value Correction |  | R2 | R4 | R6 | R8 | [15 empty] | 0.09 / 0.15 |  |  | 0.65895 |  |  | R-Value Correction |  | R2 | R4 | R6 | R8 | [8 empty] | 0.09 / 0.15 |  |  | 0.6584 |  |  | R-Value Correction |  | R2 | R4 | R6 | R8 | [8 empty] | 0.09 / 0.15 |  |  | 0.66072 |  |  | R-Value Correction |  | R2 | R4 | R6 | R8 | [8 empty] | 0.09 / 0.15 |  |  | 0.66303
|  |  | 1.951 | 1.2692 | 1 | 0.85111 |  | R-Value Correction |  | R2 | R4 | R6 | R8 |  | 0.12 / 0.24 |  |  | 1 | [8 empty] | (WIF - Heat Loss) |  | 1.7789 | 1.2474 | 1 | 0.87895 |  | R-Value Correction |  |  |  | R2 |  | R4 |  | R6 |  | R8 |  |  |  | 0.12 / 0.24 |  |  | 1 |  |  | (WIF - Heat Loss) |  | 1.9789 | 1.2746 | 1 | 0.84507 |  | R-Value Correction |  | R2 | R4 | R6 | R8 |  | 0.12 / 0.24 |  |  | 1 |  |  | (WIF - Heat Loss) |  | 1.951 | 1.2692 | 1 | 0.85111 |  | R-Value Correction |  | R2 | R4 | R6 | R8 |  | 0.12 / 0.24 |  |  | 1 |  |  | (WIF - Heat Loss) |  | 1.9231 | 1.2637 | 1 | 0.85714 |  | R-Value Correction |  | R2 | R4 | R6 | R8 |  | 0.12 / 0.24 |  |  | 1
[10 empty] | 2.0117 | 1.2557 | 1 | 0.84255 |  | 0.24 / 0.47 |  |  | 2.0469 | [15 empty] | (WIF - Sensible Gain) |  |  |  | 1.8203 |  | 1.25 |  | 1 |  | 0.85938 |  |  |  | 0.24 / 0.47 |  |  | 2.0699 | [9 empty] | (WIF - Sensible Gain) |  | 2.0154 | 1.2256 | 1 | 0.8359 |  | 0.24 / 0.47 |  |  | 2.0501 | [9 empty] | (WIF - Sensible Gain) |  | 2.0117 | 1.2557 | 1 | 0.84255 |  | 0.24 / 0.47 |  |  | 2.0469 | [9 empty] | (WIF - Sensible Gain) |  | 2.0079 | 1.2857 | 1 | 0.84921 |  | 0.24 / 0.47 |  |  | 2.0436
[15 empty] | 0.35 / 0.70 |  |  | 3.1222 | [29 empty] | 0.35 / 0.70 |  |  | 3.1525 | [16 empty] | 0.35 / 0.70 |  |  | 3.1331 | [16 empty] | 0.35 / 0.70 |  |  | 3.1222 | [16 empty] | 0.35 / 0.70 |  |  | 3.1113
| Leakage Correction (LCF) for Heat Loss | [6 empty] | Leakage Correction (LCF) for Sensible Gain | [18 empty] | Leakage Correction (LCF) for Heat Loss | [6 empty] | Leakage Correction (LCF) for Sensible Gain | [13 empty] | Surface Area Adjustment (LGA) for Latent Gain | [5 empty] | Leakage Correction (LCF) for Heat Loss | [6 empty] | Leakage Correction (LCF) for Sensible Gain | [6 empty] | Surface Area Adjustment (LGA) for Latent Gain | [5 empty] | Leakage Correction (LCF) for Heat Loss | [6 empty] | Leakage Correction (LCF) for Sensible Gain | [6 empty] | Surface Area Adjustment (LGA) for Latent Gain | [5 empty] | Leakage Correction (LCF) for Heat Loss | [6 empty] | Leakage Correction (LCF) for Sensible Gain | [6 empty] | Surface Area Adjustment (LGA) for Latent Gain
| Leakage | R2 | R4 | R6 | R8 |  |  | Leakage | R2 | R4 | R6 | R8 | [14 empty] | Leakage | R2 | R4 | R6 | R8 |  |  | Leakage |  | R2 |  | R4 |  | R6 |  | R8 | [5 empty] | Return side LGA = Actual return-side area / Default return-side area | [5 empty] | Leakage | R2 | R4 | R6 | R8 |  |  | Leakage | R2 | R4 | R6 | R8 |  |  | Return side LGA = Actual return-side area / Default return-side area | [5 empty] | Leakage | R2 | R4 | R6 | R8 |  |  | Leakage | R2 | R4 | R6 | R8 |  |  | Return side LGA = Actual return-side area / Default return-side area | [5 empty] | Leakage | R2 | R4 | R6 | R8 |  |  | Leakage | R2 | R4 | R6 | R8 |  |  | Return side LGA = Actual return-side area / Default return-side area
| 0.06 / 0.06 | 0.87856 | 0.83612 | 0.77328 | 0.73826 |  |  | 0.06 / 0.06 | 0.84338 | 0.79212 | 0.74733 | 0.70321 | [14 empty] | 0.06 / 0.06 | 0.88206 | 0.83529 | 0.79338 | 0.75212 |  |  | 0.06 / 0.06 |  | 0.8503 |  | 0.79366 |  | 0.75159 |  | 0.71178 | [11 empty] | 0.06 / 0.06 | 0.8774 | 0.82319 | 0.77105 | 0.74077 |  |  | 0.06 / 0.06 | 0.85059 | 0.79351 | 0.7443 | 0.69903 | [8 empty] | 0.06 / 0.06 | 0.87856 | 0.83612 | 0.77328 | 0.73826 |  |  | 0.06 / 0.06 | 0.84338 | 0.79212 | 0.74733 | 0.70321 | [8 empty] | 0.06 / 0.06 | 0.87972 | 0.84905 | 0.7755 | 0.73576 |  |  | 0.06 / 0.06 | 0.83617 | 0.79072 | 0.75035 | 0.70739
| 0.09 / 0.15 | 0.94135 | 0.91603 | 0.88231 | 0.87253 |  |  | 0.09 / 0.15 | 0.91593 | 0.89955 | 0.87552 | 0.84937 | [14 empty] | 0.09 / 0.15 | 0.94199 | 0.91118 | 0.89247 | 0.87699 |  |  | 0.09 / 0.15 |  | 0.92213 |  | 0.89291 |  | 0.87554 |  | 0.85352 | [5 empty] | Procedure for Latent Gain Adjustment | [5 empty] | 0.09 / 0.15 | 0.93448 | 0.91445 | 0.88299 | 0.87346 |  |  | 0.09 / 0.15 | 0.92359 | 0.89444 | 0.87428 | 0.84191 |  |  | Procedure for Latent Gain Adjustment | [5 empty] | 0.09 / 0.15 | 0.94135 | 0.91603 | 0.88231 | 0.87253 |  |  | 0.09 / 0.15 | 0.91593 | 0.89955 | 0.87552 | 0.84937 |  |  | Procedure for Latent Gain Adjustment | [5 empty] | 0.09 / 0.15 | 0.94822 | 0.91761 | 0.88162 | 0.8716 |  |  | 0.09 / 0.15 | 0.90828 | 0.90466 | 0.87677 | 0.85682 |  |  | Procedure for Latent Gain Adjustment
| 0.12 / 0.24 | 1 | 1 | 1 | 1 |  |  | 0.12 / 0.24 | 1 | 1 | 1 | 1 | [14 empty] | 0.12 / 0.24 | 1 | 1 | 1 | 1 |  |  | 0.12 / 0.24 |  | 1 |  | 1 |  | 1 |  | 1 | [5 empty] | Step 1: Select the base case latent gain value (multiply by - 1.0 for negative Grains). | [5 empty] | 0.12 / 0.24 | 1 | 1 | 1 | 1 |  |  | 0.12 / 0.24 | 1 | 1 | 1 | 1 |  |  | Step 1: Select the base case latent gain value (multiply by - 1.0 for negative Grains). | [5 empty] | 0.12 / 0.24 | 1 | 1 | 1 | 1 |  |  | 0.12 / 0.24 | 1 | 1 | 1 | 1 |  |  | Step 1: Select the base case latent gain factor. | [5 empty] | 0.12 / 0.24 | 1 | 1 | 1 | 1 |  |  | 0.12 / 0.24 | 1 | 1 | 1 | 1 |  |  | Step 1: Select the base case latent gain value (multiply by - 1.0 for negative Grains).
| 0.24 / 0.47 | 1.2284 | 1.3573 | 1.4395 | 1.4939 |  |  | 0.24 / 0.47 | 1.3536 | 1.4849 | 1.5725 | 1.6604 | [14 empty] | 0.24 / 0.47 | 1.21 | 1.3398 | 1.3998 | 1.4656 |  |  | 0.24 / 0.47 |  | 1.3383 |  | 1.4747 |  | 1.5881 |  | 1.6564 | [5 empty] | Step 2: Apply leakage correction to the Step 1 value. | [5 empty] | 0.24 / 0.47 | 1.2259 | 1.3279 | 1.4229 | 1.4813 |  |  | 0.24 / 0.47 | 1.3537 | 1.4654 | 1.5703 | 1.6412 |  |  | Step 2: Apply leakage correction to the Step 1 value. | [5 empty] | 0.24 / 0.47 | 1.2284 | 1.3573 | 1.4395 | 1.4939 |  |  | 0.24 / 0.47 | 1.3536 | 1.4849 | 1.5725 | 1.6604 |  |  | Step 2: Apply leakage correction to the Step 1 value. | [5 empty] | 0.24 / 0.47 | 1.2309 | 1.3867 | 1.456 | 1.5065 |  |  | 0.24 / 0.47 | 1.3535 | 1.5044 | 1.5747 | 1.6797 |  |  | Step 2: Apply leakage correction to the Step 1 value.
| 0.35 / 0.70 | 1.4992 | 1.7361 | 1.9119 | 2.053 |  |  | 0.35 / 0.70 | 1.7013 | 1.9676 | 2.1408 | 2.3208 | [14 empty] | 0.35 / 0.70 | 1.4301 | 1.6443 | 1.8189 | 1.9559 |  |  | 0.35 / 0.70 |  | 1.6757 |  | 1.9596 |  | 2.1706 |  | 2.3256 | [5 empty] | Step 3: Apply surface area adjustment to the Step 2 value. | [5 empty] | 0.35 / 0.70 | 1.4721 | 1.7005 | 1.8575 | 2.0192 |  |  | 0.35 / 0.70 | 1.6987 | 1.9523 | 2.1498 | 2.3003 |  |  | Step 3: Apply surface area adjustment to the Step 2 value. | [5 empty] | 0.35 / 0.70 | 1.4992 | 1.7361 | 1.9119 | 2.053 |  |  | 0.35 / 0.70 | 1.7013 | 1.9676 | 2.1408 | 2.3208 |  |  | Step 3: Apply surface area adjustment to the Step 2 value. | [5 empty] | 0.35 / 0.70 | 1.5262 | 1.7716 | 1.9662 | 2.0868 |  |  | 0.35 / 0.70 | 1.7039 | 1.9829 | 2.1318 | 2.3413 |  |  | Step 3: Apply surface area adjustment to the Step 2 value.
| Default Duct Wall Surface Area (SqFt) | [9 empty] | Surface Area Factors | [15 empty] | Default Duct Wall Surface Area (SqFt) | [12 empty] | Surface Area Factors | [13 empty] | Default Duct Wall Surface Area (SqFt) | [9 empty] | Surface Area Factors | [9 empty] | Default Duct Wall Surface Area (SqFt) | [9 empty] | Surface Area Factors | [9 empty] | Default Duct Wall Surface Area (SqFt) | [9 empty] | Surface Area Factors
[11 empty] | Leakage | Ks | Kr | [26 empty] | Leakage |  | Ks |  | Kr | [19 empty] | Leakage | Ks | Kr | [17 empty] | Leakage | Ks | Kr | [17 empty] | Leakage | Ks | Kr
| Floor Area Look-Up Value | [9 empty] | 0.06 / 0.06 | 0.83412 | 0.16588 | [13 empty] | Floor Area Look-Up Value | [12 empty] | 0.06 / 0.06 |  | 0.83909 |  | 0.16091 | [9 empty] | Floor Area Look-Up Value | [9 empty] | 0.06 / 0.06 | 0.83387 | 0.16613 | [7 empty] | Floor Area Look-Up Value | [9 empty] | 0.06 / 0.06 | 0.83412 | 0.16588 | [7 empty] | Floor Area Look-Up Value | [9 empty] | 0.06 / 0.06 | 0.83436 | 0.16564
| 3000 | 3000 | 6000 | 6000 | 9000 | 9000 | 12000 | 12000 | 15000 | 15000 | 0.09 / 0.15 | 0.81639 | 0.18361 | [13 empty] | 3,000 SqFt |  | 6,000 SqFt |  | 9,000 SqFt |  | 12,000 SqFt |  |  | 15,000 SqFt |  |  |  | 0.09 / 0.15 |  | 0.82263 |  | 0.17737 | [9 empty] | 3,000 SqFt |  | 6,000 SqFt |  | 9,000 SqFt |  | 12,000 SqFt |  | 15,000 SqFt |  | 0.09 / 0.15 | 0.81644 | 0.18356 | [7 empty] | 3,000 SqFt |  | 6,000 SqFt |  | 9,000 SqFt |  | 12,000 SqFt |  | 15,000 SqFt |  | 0.09 / 0.15 | 0.81639 | 0.18361 | [7 empty] | 3,000 SqFt |  | 6,000 SqFt |  | 9,000 SqFt |  | 12,000 SqFt |  | 15,000 SqFt |  | 0.09 / 0.15 | 0.81634 | 0.18366
| Supply | Return | Supply | Return | Supply | Return | Supply | Return | Supply | Return | 0.12 / 0.24 | 0.80051 | 0.19949 | [13 empty] | Supply | Return | Supply | Return | Supply | Return | Supply | Return |  | Supply |  | Return |  | 0.12 / 0.24 |  | 0.80777 |  | 0.19223 | [9 empty] | Supply | Return | Supply | Return | Supply | Return | Supply | Return | Supply | Return | 0.12 / 0.24 | 0.80074 | 0.19926 | [7 empty] | Supply | Return | Supply | Return | Supply | Return | Supply | Return | Supply | Return | 0.12 / 0.24 | 0.80051 | 0.19949 | [7 empty] | Supply | Return | Supply | Return | Supply | Return | Supply |  | Supply | Return | 0.12 / 0.24 | 0.80029 | 0.19971
| 954 | 205 | 2217 | 434 | 3749.5 | 730 | 5474 | 1042 | 7127.5 | 1413.5 | 0.24 / 0.47 | 0.77981 | 0.22019 | [13 empty] | 634 | 121 | 1399 | 254 | 2143 | 428 | 2988 | 610 |  | 4533 |  | 829 |  | 0.24 / 0.47 |  | 0.78869 |  | 0.21131 | [9 empty] | 764 | 170 | 1866 | 359 | 3212 | 605 | 4479 | 863 | 5832 | 1171 | 0.24 / 0.47 | 0.77869 | 0.22131 | [7 empty] | 954 | 205 | 2217 | 434 | 3749.5 | 730 | 5474 | 1042 | 7127.5 | 1413.5 | 0.24 / 0.47 | 0.77981 | 0.22019 | [7 empty] | 1144 | 240 | 2568 | 509 | 4287 | 855 | 6469 | 1221 | 8423 | 1656 | 0.24 / 0.47 | 0.78092 | 0.21908
[11 empty] | 0.35 / 0.70 | 0.76706 | 0.23294 | [13 empty] | See Section 9-9 for instruction for determining the floor area look-up value. | [12 empty] | 0.35 / 0.70 |  | 0.77406 |  | 0.22594 | [9 empty] | See Section 9-9 for instruction for determining the floor area look-up value. | [9 empty] | 0.35 / 0.70 | 0.7675 | 0.2325 | [7 empty] | See Section 9-9 for instruction for determining the floor area look-up value. | [9 empty] | 0.35 / 0.70 | 0.76706 | 0.23294 | [7 empty] | See Section 9-9 for instruction for determining the floor area look-up value. | [9 empty] | 0.35 / 0.70 | 0.76662 | 0.23338
[27 empty] | ALF | Trunk and Branch Supply and Return System Installed in a Unconditioned Space or Outdoors | [23 empty] | Table |  | ALF | Trunk and Branch Supply and Return System Installed in a Unconditioned Space or Outdoors | [16 empty] | Table |  | ALF | Trunk and Branch Supply and Return System Installed in a Unconditioned Space or Outdoors | [16 empty] | Table |  | ALF | Trunk and Branch Supply and Return System Installed in a Unconditioned Space or Outdoors | [16 empty] | Table
[27 empty] | 0.5 | Supply location = Center of Rooms |  |  |  | Number of supplies: 3,000 SF = 15; 6,000 SF = 20; 9,000 SF = 25; 12,000 SF = 30; 15,000 SF = 35 | [13 empty] | One return for four supplies; returns close to air handler | [5 empty] | 7TC-0.5 |  | 1.0 | Supply location = Center of room ceilings |  |  |  | Number of supplies: 3,000 SF = 15; 6,000 SF = 20; 9,000 SF = 25; 12,000 SF = 30; 15,000 SF = 35 | [7 empty] | One return for four supplies; returns close to air handler |  |  |  |  | 7TC-1.0 |  | 1.5 | Supply location = Center of room ceilings |  |  |  | Number of supplies: 3,000 SF = 15; 6,000 SF = 20; 9,000 SF = 25; 12,000 SF = 30; 15,000 SF = 35 | [7 empty] | One return for four supplies; returns close to air handler |  |  |  |  | 7TC-1.5 |  | 2.0 | Supply location = Center of Rooms |  |  |  | Number of supplies: 3,000 SF = 15; 6,000 SF = 20; 9,000 SF = 25; 12,000 SF = 30; 15,000 SF = 35 | [7 empty] | One return for four supplies; returns close to air handler |  |  |  |  | 7TC-2.0
[28 empty] | Duct leakage Cfm per SqFt of duct surface area (supply / return) = 0.06/0.06; 0.09/0.15; 0.12/0.24; 0.24/0.47; 0.35/0.70 | [17 empty] | Duct wall insulation R-value = 2, 4, 6 and 8 | [8 empty] | Duct leakage Cfm per SqFt of duct surface area (supply / return) = 0.06/0.06; 0.09/0.15; 0.12/0.24; 0.24/0.47; 0.35/0.70 | [11 empty] | Duct wall insulation R-value = 2, 4, 6 and 8 | [7 empty] | Duct leakage Cfm per SqFt of duct surface area (supply / return) = 0.06/0.06; 0.09/0.15; 0.12/0.24; 0.24/0.47; 0.35/0.70 | [11 empty] | Duct wall insulation R-value = 2, 4, 6 and 8 | [7 empty] | Duct leakage Cfm per SqFt of duct surface area (supply / return) = 0.06/0.06; 0.09/0.15; 0.12/0.24; 0.24/0.47; 0.35/0.70 | [11 empty] | Duct wall insulation R-value = 2, 4, 6 and 8
[27 empty] | Base Case Heat Loss Factor (BHLF) | [6 empty] | Base Case Sensible Gain Factor (BSGF) | [13 empty] | ± Btuh Values for Base Case Latent Gain (BLG) | [5 empty] | Base Case Heat Loss Factor (BHLF) | [6 empty] | Base Case Sensible Gain Factor (BSGF) | [6 empty] | ± Btuh Values for Base Case Latent Gain (BLG) | [5 empty] | Base Case Heat Loss Factor (BHLF) | [6 empty] | Base Case Sensible Gain Factor (BSGF) | [6 empty] | ± Btuh Values for Base Case Latent Gain (BLG) | [5 empty] | Base Case Heat Loss Factor (BHLF) | [6 empty] | Base Case Sensible Gain Factor (BSGF) | [6 empty] | ± Btuh Values for Base Case Latent Gain (BLG)
3 | 7TC-1.5 | Trunk and Branch Supply and Return System Installed in a Unconditioned Space or Outdoors, Center Supply Outlets | [24 empty] | R6 Insulation, ASHRAE Sealed (Supply = 0.12, Return = 0.24) | [6 empty] | R6 Insulation, ASHRAE Sealed (Supply = 0.12, Return = 0.24) | [13 empty] | R6 Insulation, ASHRAE Sealed (Supply = 0.12, Return = 0.24) | [5 empty] | R6 Insulation, ASHRAE Sealed (Supply = 0.12, Return = 0.24) | [6 empty] | R6 Insulation, ASHRAE Sealed (Supply = 0.12, Return = 0.24) | [6 empty] | R6 Insulation, ASHRAE Sealed (Supply = 0.12, Return = 0.24) | [5 empty] | R6 Insulation, ASHRAE Sealed (Supply = 0.12, Return = 0.24) | [6 empty] | R6 Insulation, ASHRAE Sealed (Supply = 0.12, Return = 0.24) | [6 empty] | R6 Insulation, ASHRAE Sealed (Supply = 0.12, Return = 0.24) | [5 empty] | R6 Insulation, ASHRAE Sealed (Supply = 0.12, Return = 0.24) | [6 empty] | R6 Insulation, ASHRAE Sealed (Supply = 0.12, Return = 0.24) | [6 empty] | R6 Insulation, ASHRAE Sealed (Supply = 0.12, Return = 0.24)
| Ambient | Square Feet of Floor Area | [5 empty] | Ambient | Square Feet of Floor Area | [5 empty] | Ambient | Square Feet of Floor Area | [10 empty] | Ambient | Square Feet of Floor Area | [5 empty] | Ambient |  | Square Feet of Floor Area | [11 empty] | Ambient | Square Feet of Floor Area |  |  |  |  | Ambient | Square Feet of Floor Area | [5 empty] | Ambient | Square Feet of Floor Area | [5 empty] | Ambient | Square Feet of Floor Area |  |  |  |  | Ambient | Square Feet of Floor Area | [5 empty] | Ambient | Square Feet of Floor Area | [5 empty] | Ambient | Square Feet of Floor Area |  |  |  |  | Ambient | Square Feet of Floor Area | [5 empty] | Ambient | Square Feet of Floor Area | [5 empty] | Ambient | Square Feet of Floor Area
| Dry Bulb | 3000 | 6000 | 9000 | 12000 | 15000 |  | Dry Bulb | 3000 | 6000 | 9000 | 12000 | 15000 |  | ∆ Grains ± | 3000 | 6000 | 9000 | 12000 | 15000 | [6 empty] | Dry Bulb | 3000 | 6000 | 9000 | 12000 | 15000 |  | Dry Bulb |  | 3000 |  | 6000 |  | 9000 |  | 12000 |  | 15000 |  |  |  | ∆ Grains ± | 3000 | 6000 | 9000 | 12000 | 15000 | Dry Bulb | 3000 | 6000 | 9000 | 12000 | 15000 |  | Dry Bulb | 3000 | 6000 | 9000 | 12000 | 15000 |  | ∆ Grains ± | 3000 | 6000 | 9000 | 12000 | 15000 | Dry Bulb | 3000 | 6000 | 9000 | 12000 | 15000 |  | Dry Bulb | 3000 | 6000 | 9000 | 12000 | 15000 |  | ∆ Grains ± | 3000 | 6000 | 9000 | 12000 | 15000 | Dry Bulb | 3000 | 6000 | 9000 | 12000 | 15000 |  | Dry Bulb | 3000 | 6000 | 9000 | 12000 | 15000 |  | ∆ Grains ± | 3000 | 6000 | 9000 | 12000 | 15000
| -20 | 0.178 | 0.18888 | 0.19975 | 0.21063 | 0.2215 |  | 60 | -0.0065 | -0.005625 | -0.00475 | -0.003875 | -0.003 |  | 10 | 1005.5 | 2201.625 | 3397.75 | 4593.875 | 5790 | [6 empty] | -20 | 0.268 | 0.28037 | 0.29275 | 0.30512 | 0.3175 |  | 60 |  | 0.001 |  | 0.0015 |  | 0.002 |  | 0.0025 |  | 0.003 |  |  |  | 10 | 575 | 1387 | 2199 | 3011 | 3823 | -20 | 0.1995 | 0.21338 | 0.22725 | 0.24113 | 0.255 |  | 60 | -0.009 | -0.00825 | -0.0075 | -0.00675 | -0.006 |  | 10 | 811 | 1770.25 | 2729.5 | 3688.75 | 4648 | -20 | 0.178 | 0.18888 | 0.19975 | 0.21063 | 0.2215 |  | 60 | -0.0065 | -0.005625 | -0.00475 | -0.003875 | -0.003 |  | 10 | 1005.5 | 2201.625 | 3397.75 | 4593.875 | 5790 | -20 | 0.1565 | 0.16437 | 0.17225 | 0.18013 | 0.188 |  | 60 | -0.004 | -0.003 | -0.002 | -0.001 | 0 |  | 10 | 1200 | 2633 | 4066 | 5499 | 6932
| -10 | 0.15933 | 0.16954 | 0.17975 | 0.18996 | 0.20017 |  | 70 | 0.0217 | 0.023813 | 0.025925 | 0.028038 | 0.03015 |  | 20 | 1613.5 | 3524.5208 | 5435.5417 | 7346.5625 | 9257.5833 | [6 empty] | -10 | 0.24 | 0.25133 | 0.26267 | 0.274 | 0.28533 |  | 70 |  | 0.0488 |  | 0.04955 |  | 0.0503 |  | 0.05105 |  | 0.0518 |  |  |  | 20 | 930.1667 | 2216.2917 | 3502.4167 | 4788.5417 | 6074.6667 | -10 | 0.178 | 0.191 | 0.204 | 0.217 | 0.23 |  | 70 | 0.0239 | 0.026075 | 0.02825 | 0.030425 | 0.0326 |  | 20 | 1309.6667 | 2855.9583 | 4402.25 | 5948.5417 | 7494.8333 | -10 | 0.15933 | 0.16954 | 0.17975 | 0.18996 | 0.20017 |  | 70 | 0.0217 | 0.023813 | 0.025925 | 0.028038 | 0.03015 |  | 20 | 1613.5 | 3524.5208 | 5435.5417 | 7346.5625 | 9257.5833 | -10 | 0.14067 | 0.14808 | 0.1555 | 0.16292 | 0.17033 |  | 70 | 0.0195 | 0.02155 | 0.0236 | 0.02565 | 0.0277 |  | 20 | 1917.3333 | 4193.0833 | 6468.8333 | 8744.5833 | 11020.3333
| 0 | 0.14067 | 0.15021 | 0.15975 | 0.16929 | 0.17883 |  | 80 | 0.0499 | 0.05325 | 0.0566 | 0.05995 | 0.0633 |  | 30 | 2221.5 | 4847.4167 | 7473.3333 | 10099.25 | 12725.1667 | [6 empty] | 0 | 0.212 | 0.22229 | 0.23258 | 0.24288 | 0.25317 |  | 80 |  | 0.0966 |  | 0.0976 |  | 0.0986 |  | 0.0996 |  | 0.1006 |  |  |  | 30 | 1285.3333 | 3045.5833 | 4805.8333 | 6566.0833 | 8326.3333 | 0 | 0.1565 | 0.16862 | 0.18075 | 0.19287 | 0.205 |  | 80 | 0.0568 | 0.0604 | 0.064 | 0.0676 | 0.0712 |  | 30 | 1808.3333 | 3941.6667 | 6075 | 8208.3333 | 10341.6667 | 0 | 0.14067 | 0.15021 | 0.15975 | 0.16929 | 0.17883 |  | 80 | 0.0499 | 0.05325 | 0.0566 | 0.05995 | 0.0633 |  | 30 | 2221.5 | 4847.4167 | 7473.3333 | 10099.25 | 12725.1667 | 0 | 0.12483 | 0.13179 | 0.13875 | 0.14571 | 0.15267 |  | 80 | 0.043 | 0.0461 | 0.0492 | 0.0523 | 0.0554 |  | 30 | 2634.6667 | 5753.1667 | 8871.6667 | 11990.1667 | 15108.6667
| 10 | 0.122 | 0.13087 | 0.13975 | 0.14863 | 0.1575 |  | 90 | 0.0781 | 0.082688 | 0.087275 | 0.091863 | 0.09645 |  | 40 | 2829.5 | 6170.3125 | 9511.125 | 12851.9375 | 16192.75 | [6 empty] | 10 | 0.184 | 0.19325 | 0.2025 | 0.21175 | 0.221 |  | 90 |  | 0.1444 |  | 0.14565 |  | 0.1469 |  | 0.14815 |  | 0.1494 |  |  |  | 40 | 1640.5 | 3874.875 | 6109.25 | 8343.625 | 10578 | 10 | 0.135 | 0.14625 | 0.1575 | 0.16875 | 0.18 |  | 90 | 0.0897 | 0.094725 | 0.09975 | 0.10478 | 0.1098 |  | 40 | 2307 | 5027.375 | 7747.75 | 10468.125 | 13188.5 | 10 | 0.122 | 0.13087 | 0.13975 | 0.14863 | 0.1575 |  | 90 | 0.0781 | 0.082688 | 0.087275 | 0.091863 | 0.09645 |  | 40 | 2829.5 | 6170.3125 | 9511.125 | 12851.9375 | 16192.75 | 10 | 0.109 | 0.1155 | 0.122 | 0.1285 | 0.135 |  | 90 | 0.0665 | 0.07065 | 0.0748 | 0.07895 | 0.0831 |  | 40 | 3352 | 7313.25 | 11274.5 | 15235.75 | 19197
| 20 | 0.10333 | 0.11154 | 0.11975 | 0.12796 | 0.13617 |  | 100 | 0.1063 | 0.11213 | 0.11795 | 0.12378 | 0.1296 |  | 50 | 3437.5 | 7493.2083 | 11548.9167 | 15604.625 | 19660.3333 | [6 empty] | 20 | 0.156 | 0.16421 | 0.17242 | 0.18063 | 0.18883 |  | 100 |  | 0.1922 |  | 0.1937 |  | 0.1952 |  | 0.1967 |  | 0.1982 |  |  |  | 50 | 1995.6667 | 4704.1667 | 7412.6667 | 10121.1667 | 12829.6667 | 20 | 0.1135 | 0.12387 | 0.13425 | 0.14462 | 0.155 |  | 100 | 0.1226 | 0.12905 | 0.1355 | 0.14195 | 0.1484 |  | 50 | 2805.6667 | 6113.0833 | 9420.5 | 12727.9167 | 16035.3333 | 20 | 0.10333 | 0.11154 | 0.11975 | 0.12796 | 0.13617 |  | 100 | 0.1063 | 0.11213 | 0.11795 | 0.12378 | 0.1296 |  | 50 | 3437.5 | 7493.2083 | 11548.9167 | 15604.625 | 19660.3333 | 20 | 0.093167 | 0.099208 | 0.10525 | 0.11129 | 0.11733 |  | 100 | 0.09 | 0.0952 | 0.1004 | 0.1056 | 0.1108 |  | 50 | 4069.3333 | 8873.3333 | 13677.3333 | 18481.3333 | 23285.3333
| 30 | 0.084667 | 0.092208 | 0.09975 | 0.10729 | 0.11483 |  | 110 | 0.1345 | 0.14156 | 0.14863 | 0.15569 | 0.16275 |  | 60 | 4045.5 | 8816.1042 | 13586.7083 | 18357.3125 | 23127.9167 | [6 empty] | 30 | 0.128 | 0.13517 | 0.14233 | 0.1495 | 0.15667 |  | 110 |  | 0.24 |  | 0.24175 |  | 0.2435 |  | 0.24525 |  | 0.247 |  |  |  | 60 | 2350.8333 | 5533.4583 | 8716.0833 | 11898.7083 | 15081.3333 | 30 | 0.092 | 0.1015 | 0.111 | 0.1205 | 0.13 |  | 110 | 0.1555 | 0.16337 | 0.17125 | 0.17913 | 0.187 |  | 60 | 3304.3333 | 7198.7917 | 11093.25 | 14987.7083 | 18882.1667 | 30 | 0.084667 | 0.092208 | 0.09975 | 0.10729 | 0.11483 |  | 110 | 0.1345 | 0.14156 | 0.14863 | 0.15569 | 0.16275 |  | 60 | 4045.5 | 8816.1042 | 13586.7083 | 18357.3125 | 23127.9167 | 30 | 0.077333 | 0.082917 | 0.0885 | 0.094083 | 0.099667 |  | 110 | 0.1135 | 0.11975 | 0.126 | 0.13225 | 0.1385 |  | 60 | 4786.6667 | 10433.4167 | 16080.1667 | 21726.9167 | 27373.6667
| 40 | 0.066 | 0.072875 | 0.07975 | 0.086625 | 0.0935 |  | 120 | 0.1627 | 0.171 | 0.1793 | 0.1876 | 0.1959 |  | 70 | 4653.5 | 10139 | 15624.5 | 21110 | 26595.5 | [6 empty] | 40 | 0.1 | 0.10612 | 0.11225 | 0.11838 | 0.1245 |  | 120 |  | 0.2878 |  | 0.2898 |  | 0.2918 |  | 0.2938 |  | 0.2958 |  |  |  | 70 | 2706 | 6362.75 | 10019.5 | 13676.25 | 17333 | 40 | 0.0705 | 0.079125 | 0.08775 | 0.096375 | 0.105 |  | 120 | 0.1884 | 0.1977 | 0.207 | 0.2163 | 0.2256 |  | 70 | 3803 | 8284.5 | 12766 | 17247.5 | 21729 | 40 | 0.066 | 0.072875 | 0.07975 | 0.086625 | 0.0935 |  | 120 | 0.1627 | 0.171 | 0.1793 | 0.1876 | 0.1959 |  | 70 | 4653.5 | 10139 | 15624.5 | 21110 | 26595.5 | 40 | 0.0615 | 0.066625 | 0.07175 | 0.076875 | 0.082 |  | 120 | 0.137 | 0.1443 | 0.1516 | 0.1589 | 0.1662 |  | 70 | 5504 | 11993.5 | 18483 | 24972.5 | 31462
| 50 | 0.047333 | 0.053542 | 0.05975 | 0.065958 | 0.072167 |  | 130 | 0.1909 | 0.20044 | 0.20998 | 0.21951 | 0.22905 | [13 empty] | 50 | 0.072 | 0.077083 | 0.082167 | 0.08725 | 0.092333 |  | 130 |  | 0.3356 |  | 0.33785 |  | 0.3401 |  | 0.34235 |  | 0.3446 |  |  |  | BLG = (1.580E-02 x Amb + 1.126E-01) x Floor Area - 1.190E+01 x Amb - 1.180E+02 | [5 empty] | 50 | 0.049 | 0.05675 | 0.0645 | 0.07225 | 0.08 |  | 130 | 0.2213 | 0.23203 | 0.24275 | 0.25348 | 0.2642 |  | BLG = (1.957E-02 x Amb + 1.241E-01) x Floor Area - 8.838E+00 x Amb - 5.988E+01 | [5 empty] | 50 | 0.047333 | 0.053542 | 0.05975 | 0.065958 | 0.072167 |  | 130 | 0.1909 | 0.20044 | 0.20998 | 0.21951 | 0.22905 |  | BLG = (ALF 1.0 Value + ALF 2.0 Value) / 2 | [5 empty] | 50 | 0.045667 | 0.050333 | 0.055 | 0.059667 | 0.064333 |  | 130 | 0.1605 | 0.16885 | 0.1772 | 0.18555 | 0.1939 |  | BLG = (2.809E-02 x Amb + 1.968E-01) x Floor Area - 1.254E+01 x Amb - 1.076E+02
| 60 | 0.028667 | 0.034208 | 0.03975 | 0.045292 | 0.050833 |  | 140 | 0.2191 | 0.22987 | 0.24065 | 0.25143 | 0.2622 | [13 empty] | 60 | 0.044 | 0.048042 | 0.052083 | 0.056125 | 0.060167 |  | 140 |  | 0.3834 |  | 0.3859 |  | 0.3884 |  | 0.3909 |  | 0.3934 | [9 empty] | 60 | 0.0275 | 0.034375 | 0.04125 | 0.048125 | 0.055 |  | 140 | 0.2542 | 0.26635 | 0.2785 | 0.29065 | 0.3028 | [7 empty] | 60 | 0.028667 | 0.034208 | 0.03975 | 0.045292 | 0.050833 |  | 140 | 0.2191 | 0.22987 | 0.24065 | 0.25143 | 0.2622 | [7 empty] | 60 | 0.029833 | 0.034042 | 0.03825 | 0.042458 | 0.046667 |  | 140 | 0.184 | 0.1934 | 0.2028 | 0.2122 | 0.2216
| 70 | 0.01 | 0.014875 | 0.01975 | 0.024625 | 0.0295 |  | 150 | 0.2473 | 0.25931 | 0.27133 | 0.28334 | 0.29535 |  | Leakage Correction (LCF) for Latent Gain | [11 empty] | 70 | 0.016 | 0.019 | 0.022 | 0.025 | 0.028 |  | 150 |  | 0.4312 |  | 0.43395 |  | 0.4367 |  | 0.43945 |  | 0.4422 |  |  |  | Leakage Correction (LCF) for Latent Gain | [5 empty] | 70 | 0.006 | 0.012 | 0.018 | 0.024 | 0.03 |  | 150 | 0.2871 | 0.30068 | 0.31425 | 0.32783 | 0.3414 |  | Leakage Correction (LCF) for Latent Gain | [5 empty] | 70 | 0.01 | 0.014875 | 0.01975 | 0.024625 | 0.0295 |  | 150 | 0.2473 | 0.25931 | 0.27133 | 0.28334 | 0.29535 |  | Leakage Correction (LCF) for Latent Gain | [5 empty] | 70 | 0.014 | 0.01775 | 0.0215 | 0.02525 | 0.029 |  | 150 | 0.2075 | 0.21795 | 0.2284 | 0.23885 | 0.2493 |  | Leakage Correction (LCF) for Latent Gain
[8 empty] | 160 | 0.2755 | 0.28875 | 0.302 | 0.31525 | 0.3285 |  | Leakage | Any R-Value | [10 empty] | BHLF = (-3.472E-08 x Amb + 3.431E-06) x Floor Area - 2.696E-03 x Amb + 2.017E-01 | [6 empty] | 160 |  | 0.479 |  | 0.482 |  | 0.485 |  | 0.488 |  | 0.491 |  |  |  | Leakage | Any R-Value |  |  |  |  | BHLF = (-2.917-08 x Amb + 4.042E-06) x Floor Area - 2.063E-03 x Amb + 1.444E-01 | [6 empty] | 160 | 0.32 | 0.335 | 0.35 | 0.365 | 0.38 |  | Leakage | Any R-Value |  |  |  |  | BHLF = (ALF 1.0 Value + ALF 2.0 Value) / 2 | [6 empty] | 160 | 0.2755 | 0.28875 | 0.302 | 0.31525 | 0.3285 |  | Leakage | Any R-Value |  |  |  |  | BHLF = (-1.528E-08 x Amb + 2.319E-06) x Floor Area - 1.538E-03 x Amb + 1.179E-01 | [6 empty] | 160 | 0.231 | 0.2425 | 0.254 | 0.2655 | 0.277 |  | Leakage | Any R-Value
[15 empty] | 0.06 / 0.06 |  |  | 0.28458 | [15 empty] | BSGF = (8.333E-09 x Amb - 3.333E-07) x Floor Area + 4.755E-03 x Amb - 2.848E-01 | [13 empty] | 0.06 / 0.06 |  |  | 0.28162 | [9 empty] | BSGF = (4.75E-08 x Amb - 2.600E-06) x Floor Area + 3.148E-03 x Amb - 1.986E-01 | [6 empty] | 0.06 / 0.06 |  |  | 0.28403 | [9 empty] | BSGF = (ALF 1.0 Value + ALF 2.0 Value) / 2 | [6 empty] | 0.06 / 0.06 |  |  | 0.28458 | [9 empty] | BSGF = (3.500E-08 x Amb - 1.767E-06) x Floor Area + 2.245E-03 x Amb - 1.397E-01 | [6 empty] | 0.06 / 0.06 |  |  | 0.28513
| R-Value Correction |  | R2 | R4 | R6 | R8 | [8 empty] | 0.09 / 0.15 |  |  | 0.63803 | [8 empty] | R-Value Correction |  | R2 | R4 | R6 | R8 | [15 empty] | 0.09 / 0.15 |  |  | 0.63487 |  |  | R-Value Correction |  | R2 | R4 | R6 | R8 | [8 empty] | 0.09 / 0.15 |  |  | 0.63774 |  |  | R-Value Correction |  | R2 | R4 | R6 | R8 | [8 empty] | 0.09 / 0.15 |  |  | 0.63803 |  |  | R-Value Correction |  | R2 | R4 | R6 | R8 | [8 empty] | 0.09 / 0.15 |  |  | 0.63832
|  |  | 2.044 | 1.3019 | 1 | 0.8362 |  | R-Value Correction |  | R2 | R4 | R6 | R8 |  | 0.12 / 0.24 |  |  | 1 | [8 empty] | (WIF - Heat Loss) |  | 2.156 | 1.3486 | 1 | 0.79817 |  | R-Value Correction |  |  |  | R2 |  | R4 |  | R6 |  | R8 |  |  |  | 0.12 / 0.24 |  |  | 1 |  |  | (WIF - Heat Loss) |  | 2.1023 | 1.3182 | 1 | 0.82955 |  | R-Value Correction |  | R2 | R4 | R6 | R8 |  | 0.12 / 0.24 |  |  | 1 |  |  | (WIF - Heat Loss) |  | 2.044 | 1.3019 | 1 | 0.8362 |  | R-Value Correction |  | R2 | R4 | R6 | R8 |  | 0.12 / 0.24 |  |  | 1 |  |  | (WIF - Heat Loss) |  | 1.9857 | 1.2857 | 1 | 0.84286 |  | R-Value Correction |  | R2 | R4 | R6 | R8 |  | 0.12 / 0.24 |  |  | 1
[10 empty] | 1.9535 | 1.2703 | 1 | 0.86087 |  | 0.24 / 0.47 |  |  | 2.0602 | [15 empty] | (WIF - Sensible Gain) |  |  |  | 1.8478 |  | 1.2522 |  | 1 |  | 0.86957 |  |  |  | 0.24 / 0.47 |  |  | 2.1146 | [9 empty] | (WIF - Sensible Gain) |  | 1.9797 | 1.277 | 1 | 0.85811 |  | 0.24 / 0.47 |  |  | 2.0725 | [9 empty] | (WIF - Sensible Gain) |  | 1.9535 | 1.2703 | 1 | 0.86087 |  | 0.24 / 0.47 |  |  | 2.0602 | [9 empty] | (WIF - Sensible Gain) |  | 1.9273 | 1.2636 | 1 | 0.86364 |  | 0.24 / 0.47 |  |  | 2.0478
[15 empty] | 0.35 / 0.70 |  |  | 3.1976 | [29 empty] | 0.35 / 0.70 |  |  | 3.3768 | [16 empty] | 0.35 / 0.70 |  |  | 3.2387 | [16 empty] | 0.35 / 0.70 |  |  | 3.1976 | [16 empty] | 0.35 / 0.70 |  |  | 3.1565
| Leakage Correction (LCF) for Heat Loss | [6 empty] | Leakage Correction (LCF) for Sensible Gain | [18 empty] | Leakage Correction (LCF) for Heat Loss | [6 empty] | Leakage Correction (LCF) for Sensible Gain | [13 empty] | Surface Area Adjustment (LGA) for Latent Gain | [5 empty] | Leakage Correction (LCF) for Heat Loss | [6 empty] | Leakage Correction (LCF) for Sensible Gain | [6 empty] | Surface Area Adjustment (LGA) for Latent Gain | [5 empty] | Leakage Correction (LCF) for Heat Loss | [6 empty] | Leakage Correction (LCF) for Sensible Gain | [6 empty] | Surface Area Adjustment (LGA) for Latent Gain | [5 empty] | Leakage Correction (LCF) for Heat Loss | [6 empty] | Leakage Correction (LCF) for Sensible Gain | [6 empty] | Surface Area Adjustment (LGA) for Latent Gain
| Leakage | R2 | R4 | R6 | R8 |  |  | Leakage | R2 | R4 | R6 | R8 | [14 empty] | Leakage | R2 | R4 | R6 | R8 |  |  | Leakage |  | R2 |  | R4 |  | R6 |  | R8 | [5 empty] | Return side LGA = Actual return-side area / Default return-side area | [5 empty] | Leakage | R2 | R4 | R6 | R8 |  |  | Leakage | R2 | R4 | R6 | R8 |  |  | Return side LGA = Actual return-side area / Default return-side area | [5 empty] | Leakage | R2 | R4 | R6 | R8 |  |  | Leakage | R2 | R4 | R6 | R8 |  |  | Return side LGA = Actual return-side area / Default return-side area | [5 empty] | Leakage | R2 | R4 | R6 | R8 |  |  | Leakage | R2 | R4 | R6 | R8 |  |  | Return side LGA = Actual return-side area / Default return-side area
| 0.06 / 0.06 | 0.90762 | 0.86973 | 0.83283 | 0.80377 |  |  | 0.06 / 0.06 | 0.8874 | 0.84483 | 0.80004 | 0.77249 | [14 empty] | 0.06 / 0.06 | 0.95346 | 0.93977 | 0.92014 | 0.91197 |  |  | 0.06 / 0.06 |  | 0.83962 |  | 0.77931 |  | 0.73372 |  | 0.69994 | [11 empty] | 0.06 / 0.06 | 0.91922 | 0.89344 | 0.85239 | 0.83312 |  |  | 0.06 / 0.06 | 0.90381 | 0.87122 | 0.8278 | 0.80843 | [8 empty] | 0.06 / 0.06 | 0.90762 | 0.86973 | 0.83283 | 0.80377 |  |  | 0.06 / 0.06 | 0.8874 | 0.84483 | 0.80004 | 0.77249 | [8 empty] | 0.06 / 0.06 | 0.89601 | 0.84602 | 0.81327 | 0.77441 |  |  | 0.06 / 0.06 | 0.87098 | 0.81844 | 0.77228 | 0.73655
| 0.09 / 0.15 | 1.0064 | 1.0066 | 1.0102 | 1.0148 |  |  | 0.09 / 0.15 | 0.97498 | 0.97047 | 0.94517 | 0.94942 | [14 empty] | 0.09 / 0.15 | 1.062 | 1.0961 | 1.1173 | 1.1542 |  |  | 0.09 / 0.15 |  | 0.92319 |  | 0.90041 |  | 0.88179 |  | 0.85986 | [5 empty] | Procedure for Latent Gain Adjustment | [5 empty] | 0.09 / 0.15 | 1.0198 | 1.0299 | 1.0361 | 1.0535 |  |  | 0.09 / 0.15 | 0.98903 | 1.002 | 0.97508 | 0.99145 |  |  | Procedure for Latent Gain Adjustment | [5 empty] | 0.09 / 0.15 | 1.0064 | 1.0066 | 1.0102 | 1.0148 |  |  | 0.09 / 0.15 | 0.97498 | 0.97047 | 0.94517 | 0.94942 |  |  | Procedure for Latent Gain Adjustment | [5 empty] | 0.09 / 0.15 | 0.99292 | 0.98324 | 0.98433 | 0.97609 |  |  | 0.09 / 0.15 | 0.96092 | 0.93894 | 0.91525 | 0.90739 |  |  | Procedure for Latent Gain Adjustment
| 0.12 / 0.24 | 1 | 1 | 1 | 1 |  |  | 0.12 / 0.24 | 1 | 1 | 1 | 1 | [14 empty] | 0.12 / 0.24 | 1 | 1 | 1 | 1 |  |  | 0.12 / 0.24 |  | 1 |  | 1 |  | 1 |  | 1 | [5 empty] | Step 1: Select the base case latent gain value (multiply by - 1.0 for negative Grains). | [5 empty] | 0.12 / 0.24 | 1 | 1 | 1 | 1 |  |  | 0.12 / 0.24 | 1 | 1 | 1 | 1 |  |  | Step 1: Select the base case latent gain value (multiply by - 1.0 for negative Grains). | [5 empty] | 0.12 / 0.24 | 1 | 1 | 1 | 1 |  |  | 0.12 / 0.24 | 1 | 1 | 1 | 1 |  |  | Step 1: Select the base case latent gain value (multiply by - 1.0 for negative Grains). | [5 empty] | 0.12 / 0.24 | 1 | 1 | 1 | 1 |  |  | 0.12 / 0.24 | 1 | 1 | 1 | 1 |  |  | Step 1: Select the base case latent gain value (multiply by - 1.0 for negative Grains).
| 0.24 / 0.47 | 1.2653 | 1.4194 | 1.5202 | 1.6133 |  |  | 0.24 / 0.47 | 1.3329 | 1.4821 | 1.5731 | 1.6661 | [14 empty] | 0.24 / 0.47 | 1.2956 | 1.4515 | 1.5788 | 1.6972 |  |  | 0.24 / 0.47 |  | 1.3436 |  | 1.4461 |  | 1.5358 |  | 1.613 | [5 empty] | Step 2: Apply leakage correction to the Step 1 value. | [5 empty] | 0.24 / 0.47 | 1.259 | 1.4405 | 1.5378 | 1.646 |  |  | 0.24 / 0.47 | 1.3516 | 1.5221 | 1.6159 | 1.723 |  |  | Step 2: Apply leakage correction to the Step 1 value. | [5 empty] | 0.24 / 0.47 | 1.2653 | 1.4194 | 1.5202 | 1.6133 |  |  | 0.24 / 0.47 | 1.3329 | 1.4821 | 1.5731 | 1.6661 |  |  | Step 2: Apply leakage correction to the Step 1 value. | [5 empty] | 0.24 / 0.47 | 1.2717 | 1.3983 | 1.5026 | 1.5805 |  |  | 0.24 / 0.47 | 1.3142 | 1.4421 | 1.5302 | 1.6092 |  |  | Step 2: Apply leakage correction to the Step 1 value.
| 0.35 / 0.70 | 1.5397 | 1.8284 | 2.0457 | 2.225 |  |  | 0.35 / 0.70 | 1.6408 | 1.922 | 2.1075 | 2.2972 | [14 empty] | 0.35 / 0.70 | 1.5759 | 1.8937 | 2.1569 | 2.3973 |  |  | 0.35 / 0.70 |  | 1.7005 |  | 1.934 |  | 2.1275 |  | 2.2731 | [5 empty] | Step 3: Apply surface area adjustment to the Step 2 value. | [5 empty] | 0.35 / 0.70 | 1.5414 | 1.8637 | 2.0838 | 2.2934 |  |  | 0.35 / 0.70 | 1.6697 | 1.9753 | 2.1437 | 2.355 |  |  | Step 3: Apply surface area adjustment to the Step 2 value. | [5 empty] | 0.35 / 0.70 | 1.5397 | 1.8284 | 2.0457 | 2.225 |  |  | 0.35 / 0.70 | 1.6408 | 1.922 | 2.1075 | 2.2972 |  |  | Step 3: Apply surface area adjustment to the Step 2 value. | [5 empty] | 0.35 / 0.70 | 1.538 | 1.793 | 2.0076 | 2.1566 |  |  | 0.35 / 0.70 | 1.6118 | 1.8686 | 2.0713 | 2.2393 |  |  | Step 3: Apply surface area adjustment to the Step 2 value.
| Default Duct Wall Surface Area (SqFt) | [9 empty] | Surface Area Factors | [15 empty] | Default Duct Wall Surface Area (SqFt) | [12 empty] | Surface Area Factors | [13 empty] | Default Duct Wall Surface Area (SqFt) | [9 empty] | Surface Area Factors | [9 empty] | Default Duct Wall Surface Area (SqFt) | [9 empty] | Surface Area Factors | [9 empty] | Default Duct Wall Surface Area (SqFt) | [9 empty] | Surface Area Factors
[11 empty] | Leakage | Ks | Kr | [26 empty] | Leakage |  | Ks |  | Kr | [19 empty] | Leakage | Ks | Kr | [17 empty] | Leakage | Ks | Kr | [17 empty] | Leakage | Ks | Kr
| Floor Area Look-Up Value | [9 empty] | 0.06 / 0.06 | 0.66117 | 0.33883 | [13 empty] | Floor Area Look-Up Value | [12 empty] | 0.06 / 0.06 |  | 0.66654 |  | 0.33346 | [9 empty] | Floor Area Look-Up Value | [9 empty] | 0.06 / 0.06 | 0.65704 | 0.34296 | [7 empty] | Floor Area Look-Up Value | [9 empty] | 0.06 / 0.06 | 0.66117 | 0.33883 | [7 empty] | Floor Area Look-Up Value | [9 empty] | 0.06 / 0.06 | 0.6653 | 0.3347
| 3000 | 3000 | 6000 | 6000 | 9000 | 9000 | 12000 | 12000 | 15000 | 15000 | 0.09 / 0.15 | 0.63024 | 0.36976 | [13 empty] | 3,000 SqFt |  | 6,000 SqFt |  | 9,000 SqFt |  | 12,000 SqFt |  |  | 15,000 SqFt |  |  |  | 0.09 / 0.15 |  | 0.63546 |  | 0.36454 | [9 empty] | 3,000 SqFt |  | 6,000 SqFt |  | 9,000 SqFt |  | 12,000 SqFt |  | 15,000 SqFt |  | 0.09 / 0.15 | 0.62596 | 0.37404 | [7 empty] | 3,000 SqFt |  | 6,000 SqFt |  | 9,000 SqFt |  | 12,000 SqFt |  | 15,000 SqFt |  | 0.09 / 0.15 | 0.63024 | 0.36976 | [7 empty] | 3,000 SqFt |  | 6,000 SqFt |  | 9,000 SqFt |  | 12,000 SqFt |  | 15,000 SqFt |  | 0.09 / 0.15 | 0.63452 | 0.36548
| Supply | Return | Supply | Return | Supply | Return | Supply | Return | Supply | Return | 0.12 / 0.24 | 0.60641 | 0.39359 | [13 empty] | Supply | Return | Supply | Return | Supply | Return | Supply | Return |  | Supply |  | Return |  | 0.12 / 0.24 |  | 0.61481 |  | 0.38519 | [9 empty] | Supply | Return | Supply | Return | Supply | Return | Supply | Return | Supply | Return | 0.12 / 0.24 | 0.60184 | 0.39816 | [7 empty] | Supply | Return | Supply | Return | Supply | Return | Supply | Return | Supply | Return | 0.12 / 0.24 | 0.60641 | 0.39359 | [7 empty] | Supply | Return | Supply | Return | Supply | Return | Supply | Return | Supply | Return | 0.12 / 0.24 | 0.61098 | 0.38902
| 788.5 | 409.5 | 1675.5 | 844 | 2608.5 | 1336.5 | 3589 | 1823.5 | 4575 | 2339 | 0.24 / 0.47 | 0.58034 | 0.41966 | [13 empty] | 485 | 241 | 1010 | 499 | 1513 | 770 | 2041 | 1048 |  | 2781 |  | 1358 |  | 0.24 / 0.47 |  | 0.58623 |  | 0.41377 | [9 empty] | 646 | 339 | 1397 | 699 | 2192 | 1146 | 2958 | 1571 | 3770 | 2003 | 0.24 / 0.47 | 0.57624 | 0.42376 | [7 empty] | 788.5 | 409.5 | 1675.5 | 844 | 2608.5 | 1336.5 | 3589 | 1823.5 | 4575 | 2339 | 0.24 / 0.47 | 0.58034 | 0.41966 | [7 empty] | 931 | 480 | 1954 | 989 | 3025 | 1527 | 4220 | 2076 | 5380 | 2675 | 0.24 / 0.47 | 0.58445 | 0.41555
[11 empty] | 0.35 / 0.70 | 0.56104 | 0.43896 | [13 empty] | See Section 9-9 for instruction for determining the floor area look-up value. | [12 empty] | 0.35 / 0.70 |  | 0.56581 |  | 0.43419 | [9 empty] | See Section 9-9 for instruction for determining the floor area look-up value. | [9 empty] | 0.35 / 0.70 | 0.55631 | 0.44369 | [7 empty] | See Section 9-9 for instruction for determining the floor area look-up value. | [9 empty] | 0.35 / 0.70 | 0.56104 | 0.43896 | [7 empty] | See Section 9-9 for instruction for determining the floor area look-up value. | [9 empty] | 0.35 / 0.70 | 0.56577 | 0.43423
[27 empty] | ALF | Trunk and Branch Supply and Return System Installed in a Unconditioned Space or Outdoors | [23 empty] | Table |  | ALF | Trunk and Branch Supply and Return System Installed in a Unconditioned Space or Outdoors | [16 empty] | Table |  | ALF | Trunk and Branch Supply and Return System Installed in a Unconditioned Space or Outdoors | [16 empty] | Table |  | ALF | Trunk and Branch Supply and Return System Installed in a Unconditioned Space or Outdoors | [16 empty] | Table
[27 empty] | 0.5 | Supply location = Perimeter of floor plan |  |  |  | Number of supplies: 3,000 SF = 15; 6,000 SF = 20; 9,000 SF = 25; 12,000 SF = 30; 15,000 SF = 35 | [13 empty] | One return for four supplies; returns close to air handler | [5 empty] | 7TP-0.5 |  | 1.0 | Supply location = Perimeter of floor plan |  |  |  | Number of supplies: 3,000 SF = 15; 6,000 SF = 20; 9,000 SF = 25; 12,000 SF = 30; 15,000 SF = 35 | [7 empty] | One return for four supplies; returns close to air handler |  |  |  |  | 7TP-1.0 |  | 1.5 | Supply location = Perimeter of floor plan |  |  |  | Number of supplies: 3,000 SF = 15; 6,000 SF = 20; 9,000 SF = 25; 12,000 SF = 30; 15,000 SF = 35 | [7 empty] | One return for four supplies; returns close to air handler |  |  |  |  | 7TP-1.5 |  | 2.0 | Supply location = Perimeter of floor plan |  |  |  | Number of supplies: 3,000 SF = 15; 6,000 SF = 20; 9,000 SF = 25; 12,000 SF = 30; 15,000 SF = 35 | [7 empty] | One return for four supplies; returns close to air handler |  |  |  |  | 7TP-2.0
[28 empty] | Duct leakage Cfm per SqFt of duct surface area (supply / return) = 0.06/0.06; 0.09/0.15; 0.12/0.24; 0.24/0.47; 0.35/0.70 | [17 empty] | Duct wall insulation R-value = 2, 4, 6 and 8 | [8 empty] | Duct leakage Cfm per SqFt of duct surface area (supply / return) = 0.06/0.06; 0.09/0.15; 0.12/0.24; 0.24/0.47; 0.35/0.70 | [11 empty] | Duct wall insulation R-value = 2, 4, 6 and 8 | [7 empty] | Duct leakage Cfm per SqFt of duct surface area (supply / return) = 0.06/0.06; 0.09/0.15; 0.12/0.24; 0.24/0.47; 0.35/0.70 | [11 empty] | Duct wall insulation R-value = 2, 4, 6 and 8 | [7 empty] | Duct leakage Cfm per SqFt of duct surface area (supply / return) = 0.06/0.06; 0.09/0.15; 0.12/0.24; 0.24/0.47; 0.35/0.70 | [11 empty] | Duct wall insulation R-value = 2, 4, 6 and 8
[27 empty] | Base Case Heat Loss Factor (BHLF) | [6 empty] | Base Case Sensible Gain Factor (BSGF) | [13 empty] | ± Btuh Values for Base Case Latent Gain (BLG) | [5 empty] | Base Case Heat Loss Factor (BHLF) | [6 empty] | Base Case Sensible Gain Factor (BSGF) | [6 empty] | ± Btuh Values for Base Case Latent Gain (BLG) | [5 empty] | Base Case Heat Loss Factor (BHLF) | [6 empty] | Base Case Sensible Gain Factor (BSGF) | [6 empty] | ± Btuh Values for Base Case Latent Gain (BLG) | [5 empty] | Base Case Heat Loss Factor (BHLF) | [6 empty] | Base Case Sensible Gain Factor (BSGF) | [6 empty] | ± Btuh Values for Base Case Latent Gain (BLG)
3 | 7TP-1.5 | Trunk and Branch Supply and Return System Installed in a Unconditioned Space or Outdoors, Perimeter Supply Outlets | [24 empty] | R6 Insulation, ASHRAE Sealed (Supply = 0.12, Return = 0.24) | [6 empty] | R6 Insulation, ASHRAE Sealed (Supply = 0.12, Return = 0.24) | [13 empty] | R6 Insulation, ASHRAE Sealed (Supply = 0.12, Return = 0.24) | [5 empty] | R6 Insulation, ASHRAE Sealed (Supply = 0.12, Return = 0.24) | [6 empty] | R6 Insulation, ASHRAE Sealed (Supply = 0.12, Return = 0.24) | [6 empty] | R6 Insulation, ASHRAE Sealed (Supply = 0.12, Return = 0.24) | [5 empty] | R6 Insulation, ASHRAE Sealed (Supply = 0.12, Return = 0.24) | [6 empty] | R6 Insulation, ASHRAE Sealed (Supply = 0.12, Return = 0.24) | [6 empty] | R6 Insulation, ASHRAE Sealed (Supply = 0.12, Return = 0.24) | [5 empty] | R6 Insulation, ASHRAE Sealed (Supply = 0.12, Return = 0.24) | [6 empty] | R6 Insulation, ASHRAE Sealed (Supply = 0.12, Return = 0.24) | [6 empty] | R6 Insulation, ASHRAE Sealed (Supply = 0.12, Return = 0.24)
| Ambient | Square Feet of Floor Area | [5 empty] | Ambient | Square Feet of Floor Area | [5 empty] | Ambient | Square Feet of Floor Area | [10 empty] | Ambient | Square Feet of Floor Area | [5 empty] | Ambient |  | Square Feet of Floor Area | [11 empty] | Ambient | Square Feet of Floor Area |  |  |  |  | Ambient | Square Feet of Floor Area | [5 empty] | Ambient | Square Feet of Floor Area | [5 empty] | Ambient | Square Feet of Floor Area |  |  |  |  | Ambient | Square Feet of Floor Area | [5 empty] | Ambient | Square Feet of Floor Area | [5 empty] | Ambient | Square Feet of Floor Area |  |  |  |  | Ambient | Square Feet of Floor Area | [5 empty] | Ambient | Square Feet of Floor Area | [5 empty] | Ambient | Square Feet of Floor Area
| Dry Bulb | 3000 | 6000 | 9000 | 12000 | 15000 |  | Dry Bulb | 3000 | 6000 | 9000 | 12000 | 15000 |  | ∆ Grains ± | 3000 | 6000 | 9000 | 12000 | 15000 | [6 empty] | Dry Bulb | 3000 | 6000 | 9000 | 12000 | 15000 |  | Dry Bulb |  | 3000 |  | 6000 |  | 9000 |  | 12000 |  | 15000 |  |  |  | ∆ Grains ± | 3000 | 6000 | 9000 | 12000 | 15000 | Dry Bulb | 3000 | 6000 | 9000 | 12000 | 15000 |  | Dry Bulb | 3000 | 6000 | 9000 | 12000 | 15000 |  | ∆ Grains ± | 3000 | 6000 | 9000 | 12000 | 15000 | Dry Bulb | 3000 | 6000 | 9000 | 12000 | 15000 |  | Dry Bulb | 3000 | 6000 | 9000 | 12000 | 15000 |  | ∆ Grains ± | 3000 | 6000 | 9000 | 12000 | 15000 | Dry Bulb | 3000 | 6000 | 9000 | 12000 | 15000 |  | Dry Bulb | 3000 | 6000 | 9000 | 12000 | 15000 |  | ∆ Grains ± | 3000 | 6000 | 9000 | 12000 | 15000
| -20 | 0.25675 | 0.26906 | 0.28138 | 0.29369 | 0.306 |  | 60 | 0.008 | 0.00975 | 0.0115 | 0.01325 | 0.015 |  | 10 | 1276 | 2850.25 | 4424.5 | 5998.75 | 7573 | [6 empty] | -20 | 0.455 | 0.47538 | 0.49575 | 0.51613 | 0.5365 |  | 60 |  | 0.017 |  | 0.01875 |  | 0.0205 |  | 0.02225 |  | 0.024 |  |  |  | 10 | 819 | 1632.75 | 2446.5 | 3260.25 | 4074 | -20 | 0.303 | 0.3165 | 0.33 | 0.3435 | 0.357 |  | 60 | 0.009 | 0.01075 | 0.0125 | 0.01425 | 0.016 |  | 10 | 1085 | 2398.75 | 3712.5 | 5026.25 | 6340 | -20 | 0.25675 | 0.26906 | 0.28138 | 0.29369 | 0.306 |  | 60 | 0.008 | 0.00975 | 0.0115 | 0.01325 | 0.015 |  | 10 | 1276 | 2850.25 | 4424.5 | 5998.75 | 7573 | -20 | 0.2105 | 0.22162 | 0.23275 | 0.24388 | 0.255 |  | 60 | 0.007 | 0.00875 | 0.0105 | 0.01225 | 0.014 |  | 10 | 1467 | 3301.75 | 5136.5 | 6971.25 | 8806
| -10 | 0.2345 | 0.24575 | 0.257 | 0.26825 | 0.2795 |  | 70 | 0.0402 | 0.043725 | 0.04725 | 0.050775 | 0.0543 |  | 20 | 1931 | 4277.625 | 6624.25 | 8970.875 | 11317.5 | [6 empty] | -10 | 0.416 | 0.43467 | 0.45333 | 0.472 | 0.49067 |  | 70 |  | 0.0773 |  | 0.0819 |  | 0.0865 |  | 0.0911 |  | 0.0957 |  |  |  | 20 | 1238.8333 | 2595.5 | 3952.1667 | 5308.8333 | 6665.5 | -10 | 0.27633 | 0.28867 | 0.301 | 0.31333 | 0.32567 |  | 70 | 0.0457 | 0.049875 | 0.05405 | 0.058225 | 0.0624 |  | 20 | 1647.5 | 3614.5833 | 5581.6667 | 7548.75 | 9515.8333 | -10 | 0.2345 | 0.24575 | 0.257 | 0.26825 | 0.2795 |  | 70 | 0.0402 | 0.043725 | 0.04725 | 0.050775 | 0.0543 |  | 20 | 1931 | 4277.625 | 6624.25 | 8970.875 | 11317.5 | -10 | 0.19267 | 0.20283 | 0.213 | 0.22317 | 0.23333 |  | 70 | 0.0347 | 0.037575 | 0.04045 | 0.043325 | 0.0462 |  | 20 | 2214.5 | 4940.6667 | 7666.8333 | 10393 | 13119.1667
| 0 | 0.21225 | 0.22244 | 0.23263 | 0.24281 | 0.253 |  | 80 | 0.0724 | 0.0777 | 0.083 | 0.0883 | 0.0936 |  | 30 | 2586 | 5705 | 8824 | 11943 | 15062 | [6 empty] | 0 | 0.377 | 0.39396 | 0.41092 | 0.42788 | 0.44483 |  | 80 |  | 0.1376 |  | 0.14505 |  | 0.1525 |  | 0.15995 |  | 0.1674 |  |  |  | 30 | 1658.6667 | 3558.25 | 5457.8333 | 7357.4167 | 9257 | 0 | 0.24967 | 0.26083 | 0.272 | 0.28317 | 0.29433 |  | 80 | 0.0824 | 0.089 | 0.0956 | 0.1022 | 0.1088 |  | 30 | 2210 | 4830.4167 | 7450.8333 | 10071.25 | 12691.6667 | 0 | 0.21225 | 0.22244 | 0.23263 | 0.24281 | 0.253 |  | 80 | 0.0724 | 0.0777 | 0.083 | 0.0883 | 0.0936 |  | 30 | 2586 | 5705 | 8824 | 11943 | 15062 | 0 | 0.17483 | 0.18404 | 0.19325 | 0.20246 | 0.21167 |  | 80 | 0.0624 | 0.0664 | 0.0704 | 0.0744 | 0.0784 |  | 30 | 2962 | 6579.5833 | 10197.1667 | 13814.75 | 17432.3333
| 10 | 0.19 | 0.19912 | 0.20825 | 0.21737 | 0.2265 |  | 90 | 0.1046 | 0.11167 | 0.11875 | 0.12582 | 0.1329 |  | 40 | 3241 | 7132.375 | 11023.75 | 14915.125 | 18806.5 | [6 empty] | 10 | 0.338 | 0.35325 | 0.3685 | 0.38375 | 0.399 |  | 90 |  | 0.1979 |  | 0.2082 |  | 0.2185 |  | 0.2288 |  | 0.2391 |  |  |  | 40 | 2078.5 | 4521 | 6963.5 | 9406 | 11848.5 | 10 | 0.223 | 0.233 | 0.243 | 0.253 | 0.263 |  | 90 | 0.1191 | 0.12812 | 0.13715 | 0.14617 | 0.1552 |  | 40 | 2772.5 | 6046.25 | 9320 | 12593.75 | 15867.5 | 10 | 0.19 | 0.19912 | 0.20825 | 0.21737 | 0.2265 |  | 90 | 0.1046 | 0.11167 | 0.11875 | 0.12582 | 0.1329 |  | 40 | 3241 | 7132.375 | 11023.75 | 14915.125 | 18806.5 | 10 | 0.157 | 0.16525 | 0.1735 | 0.18175 | 0.19 |  | 90 | 0.0901 | 0.095225 | 0.10035 | 0.10547 | 0.1106 |  | 40 | 3709.5 | 8218.5 | 12727.5 | 17236.5 | 21745.5
| 20 | 0.16775 | 0.17581 | 0.18388 | 0.19194 | 0.2 |  | 100 | 0.1368 | 0.14565 | 0.1545 | 0.16335 | 0.1722 |  | 50 | 3896 | 8559.75 | 13223.5 | 17887.25 | 22551 | [6 empty] | 20 | 0.299 | 0.31254 | 0.32608 | 0.33963 | 0.35317 |  | 100 |  | 0.2582 |  | 0.27135 |  | 0.2845 |  | 0.29765 |  | 0.3108 |  |  |  | 50 | 2498.3333 | 5483.75 | 8469.1667 | 11454.5833 | 14440 | 20 | 0.19633 | 0.20517 | 0.214 | 0.22283 | 0.23167 |  | 100 | 0.1558 | 0.16725 | 0.1787 | 0.19015 | 0.2016 |  | 50 | 3335 | 7262.0833 | 11189.1667 | 15116.25 | 19043.3333 | 20 | 0.16775 | 0.17581 | 0.18388 | 0.19194 | 0.2 |  | 100 | 0.1368 | 0.14565 | 0.1545 | 0.16335 | 0.1722 |  | 50 | 3896 | 8559.75 | 13223.5 | 17887.25 | 22551 | 20 | 0.13917 | 0.14646 | 0.15375 | 0.16104 | 0.16833 |  | 100 | 0.1178 | 0.12405 | 0.1303 | 0.13655 | 0.1428 |  | 50 | 4457 | 9857.4167 | 15257.8333 | 20658.25 | 26058.6667
| 30 | 0.1455 | 0.1525 | 0.1595 | 0.1665 | 0.1735 |  | 110 | 0.169 | 0.17962 | 0.19025 | 0.20087 | 0.2115 |  | 60 | 4551 | 9987.125 | 15423.25 | 20859.375 | 26295.5 | [6 empty] | 30 | 0.26 | 0.27183 | 0.28367 | 0.2955 | 0.30733 |  | 110 |  | 0.3185 |  | 0.3345 |  | 0.3505 |  | 0.3665 |  | 0.3825 |  |  |  | 60 | 2918.1667 | 6446.5 | 9974.8333 | 13503.1667 | 17031.5 | 30 | 0.16967 | 0.17733 | 0.185 | 0.19267 | 0.20033 |  | 110 | 0.1925 | 0.20637 | 0.22025 | 0.23412 | 0.248 |  | 60 | 3897.5 | 8477.9167 | 13058.3333 | 17638.75 | 22219.1667 | 30 | 0.1455 | 0.1525 | 0.1595 | 0.1665 | 0.1735 |  | 110 | 0.169 | 0.17962 | 0.19025 | 0.20087 | 0.2115 |  | 60 | 4551 | 9987.125 | 15423.25 | 20859.375 | 26295.5 | 30 | 0.12133 | 0.12767 | 0.134 | 0.14033 | 0.14667 |  | 110 | 0.1455 | 0.15287 | 0.16025 | 0.16762 | 0.175 |  | 60 | 5204.5 | 11496.3333 | 17788.1667 | 24080 | 30371.8333
| 40 | 0.12325 | 0.12919 | 0.13512 | 0.14106 | 0.147 |  | 120 | 0.2012 | 0.2136 | 0.226 | 0.2384 | 0.2508 |  | 70 | 5206 | 11414.5 | 17623 | 23831.5 | 30040 | [6 empty] | 40 | 0.221 | 0.23113 | 0.24125 | 0.25138 | 0.2615 |  | 120 |  | 0.3788 |  | 0.39765 |  | 0.4165 |  | 0.43535 |  | 0.4542 |  |  |  | 70 | 3338 | 7409.25 | 11480.5 | 15551.75 | 19623 | 40 | 0.143 | 0.1495 | 0.156 | 0.1625 | 0.169 |  | 120 | 0.2292 | 0.2455 | 0.2618 | 0.2781 | 0.2944 |  | 70 | 4460 | 9693.75 | 14927.5 | 20161.25 | 25395 | 40 | 0.12325 | 0.12919 | 0.13512 | 0.14106 | 0.147 |  | 120 | 0.2012 | 0.2136 | 0.226 | 0.2384 | 0.2508 |  | 70 | 5206 | 11414.5 | 17623 | 23831.5 | 30040 | 40 | 0.1035 | 0.10887 | 0.11425 | 0.11962 | 0.125 |  | 120 | 0.1732 | 0.1817 | 0.1902 | 0.1987 | 0.2072 |  | 70 | 5952 | 13135.25 | 20318.5 | 27501.75 | 34685
| 50 | 0.101 | 0.10587 | 0.11075 | 0.11563 | 0.1205 |  | 130 | 0.2334 | 0.24757 | 0.26175 | 0.27592 | 0.2901 | [13 empty] | 50 | 0.182 | 0.19042 | 0.19883 | 0.20725 | 0.21567 |  | 130 |  | 0.4391 |  | 0.4608 |  | 0.4825 |  | 0.5042 |  | 0.5259 |  |  |  | BLG = (1.810E-02 x Amb + 9.028E-02) x Floor Area - 1.231E+01 x Amb - 1.283E+02 | [5 empty] | 50 | 0.11633 | 0.12167 | 0.127 | 0.13233 | 0.13767 |  | 130 | 0.2659 | 0.28462 | 0.30335 | 0.32207 | 0.3408 |  | BLG = (2.178E-02 x Amb + 2.201E-01) x Floor Area - 9.083E+00 x Amb - 1.379E+02 | [5 empty] | 50 | 0.101 | 0.10587 | 0.11075 | 0.11563 | 0.1205 |  | 130 | 0.2334 | 0.24757 | 0.26175 | 0.27592 | 0.2901 |  | BLG = (ALF 1.0 Value + ALF 2.0 Value) / 2 | [5 empty] | 50 | 0.085667 | 0.090083 | 0.0945 | 0.098917 | 0.10333 |  | 130 | 0.2009 | 0.21052 | 0.22015 | 0.22978 | 0.2394 |  | BLG = (2.971E-02 x Amb + 3.144E-01) x Floor Area - 1.439E+01 x Amb - 2.238E+02
| 60 | 0.07875 | 0.082562 | 0.086375 | 0.090187 | 0.094 |  | 140 | 0.2656 | 0.28155 | 0.2975 | 0.31345 | 0.3294 | [13 empty] | 60 | 0.143 | 0.14971 | 0.15642 | 0.16312 | 0.16983 |  | 140 |  | 0.4994 |  | 0.52395 |  | 0.5485 |  | 0.57305 |  | 0.5976 | [9 empty] | 60 | 0.089667 | 0.093833 | 0.098 | 0.10217 | 0.10633 |  | 140 | 0.3026 | 0.32375 | 0.3449 | 0.36605 | 0.3872 | [7 empty] | 60 | 0.07875 | 0.082562 | 0.086375 | 0.090187 | 0.094 |  | 140 | 0.2656 | 0.28155 | 0.2975 | 0.31345 | 0.3294 | [7 empty] | 60 | 0.067833 | 0.071292 | 0.07475 | 0.078208 | 0.081667 |  | 140 | 0.2286 | 0.23935 | 0.2501 | 0.26085 | 0.2716
| 70 | 0.0565 | 0.05925 | 0.062 | 0.06475 | 0.0675 |  | 150 | 0.2978 | 0.31552 | 0.33325 | 0.35097 | 0.3687 |  | Leakage Correction (LCF) for Latent Gain | [11 empty] | 70 | 0.104 | 0.109 | 0.114 | 0.119 | 0.124 |  | 150 |  | 0.5597 |  | 0.5871 |  | 0.6145 |  | 0.6419 |  | 0.6693 |  |  |  | Leakage Correction (LCF) for Latent Gain | [5 empty] | 70 | 0.063 | 0.066 | 0.069 | 0.072 | 0.075 |  | 150 | 0.3393 | 0.36287 | 0.38645 | 0.41002 | 0.4336 |  | Leakage Correction (LCF) for Latent Gain | [5 empty] | 70 | 0.0565 | 0.05925 | 0.062 | 0.06475 | 0.0675 |  | 150 | 0.2978 | 0.31552 | 0.33325 | 0.35097 | 0.3687 |  | Leakage Correction (LCF) for Latent Gain | [5 empty] | 70 | 0.05 | 0.0525 | 0.055 | 0.0575 | 0.06 |  | 150 | 0.2563 | 0.26817 | 0.28005 | 0.29192 | 0.3038 |  | Leakage Correction (LCF) for Latent Gain
[8 empty] | 160 | 0.33 | 0.3495 | 0.369 | 0.3885 | 0.408 |  | Leakage | Any R-Value | [10 empty] | BHLF = (-5.694E-08 x Amb + 5.653E-06) x Floor Area - 3.729E-03 x Amb + 3.600E-01 | [6 empty] | 160 |  | 0.62 |  | 0.65025 |  | 0.6805 |  | 0.71075 |  | 0.741 |  |  |  | Leakage | Any R-Value |  |  |  |  | BHLF = (-3.889E-08 x Amb + 3.722E-06) x Floor Area - 2.550E-03 x Amb + 2.385E-01 | [6 empty] | 160 | 0.376 | 0.402 | 0.428 | 0.454 | 0.48 |  | Leakage | Any R-Value |  |  |  |  | BHLF = (ALF 1.0 Value + ALF 2.0 Value) / 2 | [6 empty] | 160 | 0.33 | 0.3495 | 0.369 | 0.3885 | 0.408 |  | Leakage | Any R-Value |  |  |  |  | BHLF = (-3.194E-08 x Amb + 3.069E-06) x Floor Area - 1.688E-03 x Amb + 1.656E-01 | [6 empty] | 160 | 0.284 | 0.297 | 0.31 | 0.323 | 0.336 |  | Leakage | Any R-Value
[15 empty] | 0.06 / 0.06 |  |  | 0.29647 | [15 empty] | BSGF = (9.500E-08 x Amb - 5.117E-06) x Floor Area + 5.745E-03 x Amb - 3.295E-01 | [13 empty] | 0.06 / 0.06 |  |  | 0.29199 | [9 empty] | BSGF = (8.083E-08 x Amb - 4.267E-06) x Floor Area + 3.428E-03 x Amb - 1.984E-01 | [6 empty] | 0.06 / 0.06 |  |  | 0.2945 | [9 empty] | BSGF = (ALF 1.0 Value + ALF 2.0 Value) / 2 | [6 empty] | 0.06 / 0.06 |  |  | 0.29647 | [9 empty] | BSGF = (3.750E-08 x Amb - 1.667E-06) x Floor Area + 2.658E-03 x Amb - 1.542E-01 | [6 empty] | 0.06 / 0.06 |  |  | 0.29844
| R-Value Correction |  | R2 | R4 | R6 | R8 | [8 empty] | 0.09 / 0.15 |  |  | 0.64256 | [8 empty] | R-Value Correction |  | R2 | R4 | R6 | R8 | [15 empty] | 0.09 / 0.15 |  |  | 0.63583 |  |  | R-Value Correction |  | R2 | R4 | R6 | R8 | [8 empty] | 0.09 / 0.15 |  |  | 0.64129 |  |  | R-Value Correction |  | R2 | R4 | R6 | R8 | [8 empty] | 0.09 / 0.15 |  |  | 0.64256 |  |  | R-Value Correction |  | R2 | R4 | R6 | R8 | [8 empty] | 0.09 / 0.15 |  |  | 0.64383
|  |  | 1.8454 | 1.2383 | 1 | 0.86097 |  | R-Value Correction |  | R2 | R4 | R6 | R8 |  | 0.12 / 0.24 |  |  | 1 | [8 empty] | (WIF - Heat Loss) |  | 1.7468 | 1.2189 | 1 | 0.85837 |  | R-Value Correction |  |  |  | R2 |  | R4 |  | R6 |  | R8 |  |  |  | 0.12 / 0.24 |  |  | 1 |  |  | (WIF - Heat Loss) |  | 1.9236 | 1.2611 | 1 | 0.85987 |  | R-Value Correction |  | R2 | R4 | R6 | R8 |  | 0.12 / 0.24 |  |  | 1 |  |  | (WIF - Heat Loss) |  | 1.8454 | 1.2383 | 1 | 0.86097 |  | R-Value Correction |  | R2 | R4 | R6 | R8 |  | 0.12 / 0.24 |  |  | 1 |  |  | (WIF - Heat Loss) |  | 1.7672 | 1.2155 | 1 | 0.86207 |  | R-Value Correction |  | R2 | R4 | R6 | R8 |  | 0.12 / 0.24 |  |  | 1
[10 empty] | 2.0178 | 1.2964 | 1 | 0.84908 |  | 0.24 / 0.47 |  |  | 2.0894 | [15 empty] | (WIF - Sensible Gain) |  |  |  | 1.8208 |  | 1.2516 |  | 1 |  | 0.86792 |  |  |  | 0.24 / 0.47 |  |  | 2.1652 | [9 empty] | (WIF - Sensible Gain) |  | 2.1422 | 1.306 | 1 | 0.84483 |  | 0.24 / 0.47 |  |  | 2.0995 | [9 empty] | (WIF - Sensible Gain) |  | 2.0178 | 1.2964 | 1 | 0.84908 |  | 0.24 / 0.47 |  |  | 2.0894 | [9 empty] | (WIF - Sensible Gain) |  | 1.8933 | 1.2867 | 1 | 0.85333 |  | 0.24 / 0.47 |  |  | 2.0793
[15 empty] | 0.35 / 0.70 |  |  | 3.4525 | [29 empty] | 0.35 / 0.70 |  |  | 3.4816 | [16 empty] | 0.35 / 0.70 |  |  | 3.6826 | [16 empty] | 0.35 / 0.70 |  |  | 3.4525 | [16 empty] | 0.35 / 0.70 |  |  | 3.2224
| Leakage Correction (LCF) for Heat Loss | [6 empty] | Leakage Correction (LCF) for Sensible Gain | [18 empty] | Leakage Correction (LCF) for Heat Loss | [6 empty] | Leakage Correction (LCF) for Sensible Gain | [13 empty] | Surface Area Adjustment (LGA) for Latent Gain | [5 empty] | Leakage Correction (LCF) for Heat Loss | [6 empty] | Leakage Correction (LCF) for Sensible Gain | [6 empty] | Surface Area Adjustment (LGA) for Latent Gain | [5 empty] | Leakage Correction (LCF) for Heat Loss | [6 empty] | Leakage Correction (LCF) for Sensible Gain | [6 empty] | Surface Area Adjustment (LGA) for Latent Gain | [5 empty] | Leakage Correction (LCF) for Heat Loss | [6 empty] | Leakage Correction (LCF) for Sensible Gain | [6 empty] | Surface Area Adjustment (LGA) for Latent Gain
| Leakage | R2 | R4 | R6 | R8 |  |  | Leakage | R2 | R4 | R6 | R8 | [14 empty] | Leakage | R2 | R4 | R6 | R8 |  |  | Leakage |  | R2 |  | R4 |  | R6 |  | R8 | [5 empty] | Return side LGA = Actual return-side area / Default return-side area | [5 empty] | Leakage | R2 | R4 | R6 | R8 |  |  | Leakage | R2 | R4 | R6 | R8 |  |  | Return side LGA = Actual return-side area / Default return-side area | [5 empty] | Leakage | R2 | R4 | R6 | R8 |  |  | Leakage | R2 | R4 | R6 | R8 |  |  | Return side LGA = Actual return-side area / Default return-side area | [5 empty] | Leakage | R2 | R4 | R6 | R8 |  |  | Leakage | R2 | R4 | R6 | R8 |  |  | Return side LGA = Actual return-side area / Default return-side area
| 0.06 / 0.06 | 0.84368 | 0.78492 | 0.7418 | 0.68795 |  |  | 0.06 / 0.06 | 0.84043 | 0.78093 | 0.73814 | 0.70522 | [14 empty] | 0.06 / 0.06 | 0.84221 | 0.77814 | 0.72964 | 0.69135 |  |  | 0.06 / 0.06 |  | 0.82526 |  | 0.77168 |  | 0.72715 |  | 0.69634 | [11 empty] | 0.06 / 0.06 | 0.8451 | 0.77967 | 0.73024 | 0.68369 |  |  | 0.06 / 0.06 | 0.83186 | 0.77597 | 0.74119 | 0.70353 | [8 empty] | 0.06 / 0.06 | 0.84368 | 0.78492 | 0.7418 | 0.68795 |  |  | 0.06 / 0.06 | 0.84043 | 0.78093 | 0.73814 | 0.70522 | [8 empty] | 0.06 / 0.06 | 0.84225 | 0.79016 | 0.75336 | 0.69221 |  |  | 0.06 / 0.06 | 0.84901 | 0.7859 | 0.7351 | 0.70692
| 0.09 / 0.15 | 0.9178 | 0.89224 | 0.86088 | 0.84099 |  |  | 0.09 / 0.15 | 0.91797 | 0.89646 | 0.87015 | 0.85067 | [14 empty] | 0.09 / 0.15 | 0.91419 | 0.88923 | 0.8716 | 0.84287 |  |  | 0.09 / 0.15 |  | 0.9085 |  | 0.88282 |  | 0.85983 |  | 0.8449 | [5 empty] | Procedure for Latent Gain Adjustment | [5 empty] | 0.09 / 0.15 | 0.91562 | 0.88341 | 0.85838 | 0.84021 |  |  | 0.09 / 0.15 | 0.91566 | 0.89475 | 0.8746 | 0.84682 |  |  | Procedure for Latent Gain Adjustment | [5 empty] | 0.09 / 0.15 | 0.9178 | 0.89224 | 0.86088 | 0.84099 |  |  | 0.09 / 0.15 | 0.91797 | 0.89646 | 0.87015 | 0.85067 |  |  | Procedure for Latent Gain Adjustment | [5 empty] | 0.09 / 0.15 | 0.91998 | 0.90107 | 0.86338 | 0.84176 |  |  | 0.09 / 0.15 | 0.92028 | 0.89818 | 0.8657 | 0.85453 |  |  | Procedure for Latent Gain Adjustment
| 0.12 / 0.24 | 1 | 1 | 1 | 1 |  |  | 0.12 / 0.24 | 1 | 1 | 1 | 1 | [14 empty] | 0.12 / 0.24 | 1 | 1 | 1 | 1 |  |  | 0.12 / 0.24 |  | 1 |  | 1 |  | 1 |  | 1 | [5 empty] | Step 1: Select the base case latent gain value (multiply by - 1.0 for negative Grains). | [5 empty] | 0.12 / 0.24 | 1 | 1 | 1 | 1 |  |  | 0.12 / 0.24 | 1 | 1 | 1 | 1 |  |  | Step 1: Select the base case latent gain value (multiply by - 1.0 for negative Grains). | [5 empty] | 0.12 / 0.24 | 1 | 1 | 1 | 1 |  |  | 0.12 / 0.24 | 1 | 1 | 1 | 1 |  |  | Step 1: Select the base case latent gain value (multiply by - 1.0 for negative Grains). | [5 empty] | 0.12 / 0.24 | 1 | 1 | 1 | 1 |  |  | 0.12 / 0.24 | 1 | 1 | 1 | 1 |  |  | Step 1: Select the base case latent gain value (multiply by - 1.0 for negative Grains).
| 0.24 / 0.47 | 1.2259 | 1.3418 | 1.4113 | 1.4744 |  |  | 0.24 / 0.47 | 1.3373 | 1.4573 | 1.5455 | 1.6212 | [14 empty] | 0.24 / 0.47 | 1.2337 | 1.3372 | 1.4263 | 1.4815 |  |  | 0.24 / 0.47 |  | 1.3468 |  | 1.4869 |  | 1.5737 |  | 1.6531 | [5 empty] | Step 2: Apply leakage correction to the Step 1 value. | [5 empty] | 0.24 / 0.47 | 1.2399 | 1.338 | 1.4231 | 1.465 |  |  | 0.24 / 0.47 | 1.3341 | 1.4495 | 1.5398 | 1.6032 |  |  | Step 2: Apply leakage correction to the Step 1 value. | [5 empty] | 0.24 / 0.47 | 1.2259 | 1.3418 | 1.4113 | 1.4744 |  |  | 0.24 / 0.47 | 1.3373 | 1.4573 | 1.5455 | 1.6212 |  |  | Step 2: Apply leakage correction to the Step 1 value. | [5 empty] | 0.24 / 0.47 | 1.2119 | 1.3457 | 1.3994 | 1.4838 |  |  | 0.24 / 0.47 | 1.3405 | 1.4651 | 1.5512 | 1.6392 |  |  | Step 2: Apply leakage correction to the Step 1 value.
| 0.35 / 0.70 | 1.4863 | 1.6963 | 1.8489 | 1.9777 |  |  | 0.35 / 0.70 | 1.6631 | 1.9186 | 2.1034 | 2.2553 | [14 empty] | 0.35 / 0.70 | 1.4778 | 1.6908 | 1.8661 | 1.9725 |  |  | 0.35 / 0.70 |  | 1.7015 |  | 1.9749 |  | 2.1743 |  | 2.3398 | [5 empty] | Step 3: Apply surface area adjustment to the Step 2 value. | [5 empty] | 0.35 / 0.70 | 1.4988 | 1.704 | 1.8687 | 1.9853 |  |  | 0.35 / 0.70 | 1.6579 | 1.9172 | 2.1168 | 2.2421 |  |  | Step 3: Apply surface area adjustment to the Step 2 value. | [5 empty] | 0.35 / 0.70 | 1.4863 | 1.6963 | 1.8489 | 1.9777 |  |  | 0.35 / 0.70 | 1.6631 | 1.9186 | 2.1034 | 2.2553 |  |  | Step 3: Apply surface area adjustment to the Step 2 value. | [5 empty] | 0.35 / 0.70 | 1.4737 | 1.6885 | 1.8291 | 1.9701 |  |  | 0.35 / 0.70 | 1.6683 | 1.9201 | 2.0899 | 2.2686 |  |  | Step 3: Apply surface area adjustment to the Step 2 value.
| Default Duct Wall Surface Area (SqFt) | [9 empty] | Surface Area Factors | [15 empty] | Default Duct Wall Surface Area (SqFt) | [12 empty] | Surface Area Factors | [13 empty] | Default Duct Wall Surface Area (SqFt) | [9 empty] | Surface Area Factors | [9 empty] | Default Duct Wall Surface Area (SqFt) | [9 empty] | Surface Area Factors | [9 empty] | Default Duct Wall Surface Area (SqFt) | [9 empty] | Surface Area Factors
[11 empty] | Leakage | Ks | Kr | [26 empty] | Leakage |  | Ks |  | Kr | [19 empty] | Leakage | Ks | Kr | [17 empty] | Leakage | Ks | Kr | [17 empty] | Leakage | Ks | Kr
| Floor Area Look-Up Value | [9 empty] | 0.06 / 0.06 | 0.73439 | 0.26561 | [13 empty] | Floor Area Look-Up Value | [12 empty] | 0.06 / 0.06 |  | 0.66267 |  | 0.33733 | [9 empty] | Floor Area Look-Up Value | [9 empty] | 0.06 / 0.06 | 0.72552 | 0.27448 | [7 empty] | Floor Area Look-Up Value | [9 empty] | 0.06 / 0.06 | 0.73439 | 0.26561 | [7 empty] | Floor Area Look-Up Value | [9 empty] | 0.06 / 0.06 | 0.74327 | 0.25673
| 3000 | 3000 | 6000 | 6000 | 9000 | 9000 | 12000 | 12000 | 15000 | 15000 | 0.09 / 0.15 | 0.70872 | 0.29128 | [13 empty] | 3,000 SqFt |  | 6,000 SqFt |  | 9,000 SqFt |  | 12,000 SqFt |  |  | 15,000 SqFt |  |  |  | 0.09 / 0.15 |  | 0.6316 |  | 0.3684 | [9 empty] | 3,000 SqFt |  | 6,000 SqFt |  | 9,000 SqFt |  | 12,000 SqFt |  | 15,000 SqFt |  | 0.09 / 0.15 | 0.69948 | 0.30052 | [7 empty] | 3,000 SqFt |  | 6,000 SqFt |  | 9,000 SqFt |  | 12,000 SqFt |  | 15,000 SqFt |  | 0.09 / 0.15 | 0.70872 | 0.29128 | [7 empty] | 3,000 SqFt |  | 6,000 SqFt |  | 9,000 SqFt |  | 12,000 SqFt |  | 15,000 SqFt |  | 0.09 / 0.15 | 0.71796 | 0.28204
| Supply | Return | Supply | Return | Supply | Return | Supply | Return | Supply | Return | 0.12 / 0.24 | 0.68593 | 0.31407 | [13 empty] | Supply | Return | Supply | Return | Supply | Return | Supply | Return |  | Supply |  | Return |  | 0.12 / 0.24 |  | 0.60943 |  | 0.39057 | [9 empty] | Supply | Return | Supply | Return | Supply | Return | Supply | Return | Supply | Return | 0.12 / 0.24 | 0.67721 | 0.32279 | [7 empty] | Supply | Return | Supply | Return | Supply | Return | Supply | Return | Supply | Return | 0.12 / 0.24 | 0.68593 | 0.31407 | [7 empty] | Supply | Return | Supply | Return | Supply | Return | Supply | Return | Supply | Return | 0.12 / 0.24 | 0.69466 | 0.30534
| 1133.5 | 424.5 | 2354 | 879.5 | 3880.5 | 1368.5 | 5393 | 1866.5 | 6922.5 | 2415 | 0.24 / 0.47 | 0.66264 | 0.33736 | [13 empty] | 710 | 360 | 1497 | 754 | 2242 | 1168 | 3037 | 1608 |  | 4259 |  | 2065 |  | 0.24 / 0.47 |  | 0.58139 |  | 0.41861 | [9 empty] | 923 | 369 | 2050 | 770 | 3276 | 1210 | 4436 | 1657 | 5693 | 2128 | 0.24 / 0.47 | 0.65267 | 0.34733 | [7 empty] | 1133.5 | 424.5 | 2354 | 879.5 | 3880.5 | 1368.5 | 5393 | 1866.5 | 6922.5 | 2415 | 0.24 / 0.47 | 0.66264 | 0.33736 | [7 empty] | 1344 | 480 | 2658 | 989 | 4485 | 1527 | 6350 | 2076 | 8152 | 2702 | 0.24 / 0.47 | 0.67261 | 0.32739
[11 empty] | 0.35 / 0.70 | 0.64431 | 0.35569 | [26 empty] | 0.35 / 0.70 |  | 0.56254 |  | 0.43746 | [19 empty] | 0.35 / 0.70 | 0.63403 | 0.36597 | [17 empty] | 0.35 / 0.70 | 0.64431 | 0.35569 | [17 empty] | 0.35 / 0.70 | 0.65459 | 0.34541
[27 empty] | ALF | Radial or Spider Supply System Installed Under a Ground Slab, Return in Conditioned Space | [23 empty] | Table |  | ALF | Radial or Spider Supply System Installed Under a Ground Slab, Return in Conditioned Space | [16 empty] | Table |  | ALF | Radial or Spider Supply System Installed Under a Ground Slab, Return in Conditioned Space | [16 empty] | Table |  | ALF | Radial or Spider Supply System Installed Under a Ground Slab, Return in Conditioned Space | [16 empty] | Table
[27 empty] | 0.5 | Supply location = Perimeter of floor plan |  |  |  | Number of supplies: 3,000 SF = 15; 6,000 SF = 20; 9,000 SF = 25; 12,000 SF = 30; 15,000 SF = 35 | [13 empty] | One return for four supplies; returns close to air handler | [5 empty] | 7GSC-0.5 |  | 1.0 | Supply location = Perimeter of floor plan |  |  |  | Number of supplies: 3,000 SF = 15; 6,000 SF = 20; 9,000 SF = 25; 12,000 SF = 30; 15,000 SF = 35 | [7 empty] | One return for four supplies; returns close to air handler |  |  |  |  | 7GSC-1.0 |  | 1.5 | Supply location = Perimeter of floor plan |  |  |  | Number of supplies: 3,000 SF = 15; 6,000 SF = 20; 9,000 SF = 25; 12,000 SF = 30; 15,000 SF = 35 | [7 empty] | One return for four supplies; returns close to air handler |  |  |  |  | 7GSC-1.5 |  | 2.0 | Supply location = Perimeter of floor plan |  |  |  | Number of supplies: 3,000 SF = 15; 6,000 SF = 20; 9,000 SF = 25; 12,000 SF = 30; 15,000 SF = 35 | [7 empty] | One return for four supplies; returns close to air handler |  |  |  |  | 7GSC-2.0
[28 empty] | Duct leakage Cfm per SqFt of supply duct surface area = No leakage | [17 empty] | Duct wall insulation R-value = None | [8 empty] | Duct leakage Cfm per SqFt of supply duct surface area = No leakage | [11 empty] | Duct wall insulation R-value = None | [7 empty] | Duct leakage Cfm per SqFt of supply duct surface area = No leakage | [11 empty] | Duct wall insulation R-value = None | [7 empty] | Duct leakage Cfm per SqFt of supply duct surface area = No leakage | [11 empty] | Duct wall insulation R-value = None
[27 empty] | Base Case Heat Loss Factor (BHLF) | [6 empty] | Base Case Sensible Gain Factor (BSGF) | [13 empty] | ± Btuh Values for Base Case Latent Gain (BLG) | [5 empty] | Base Case Heat Loss Factor (BHLF) | [6 empty] | Base Case Sensible Gain Factor (BSGF) | [6 empty] | ± Btuh Values for Base Case Latent Gain (BLG) | [5 empty] | Base Case Heat Loss Factor (BHLF) | [6 empty] | Base Case Sensible Gain Factor (BSGF) | [6 empty] | ± Btuh Values for Base Case Latent Gain (BLG) | [5 empty] | Base Case Heat Loss Factor (BHLF) | [6 empty] | Base Case Sensible Gain Factor (BSGF) | [6 empty] | ± Btuh Values for Base Case Latent Gain (BLG)
3 | 7GSC-1.5 | Radial or Spider Supply System Installed Under a Ground Slab, Return in Conditioned Space | [24 empty] | No Insulation, No Leakage | [6 empty] | No Insulation, No Leakage | [13 empty] | No Insulation, No Leakage | [5 empty] | No Insulation, No Leakage | [6 empty] | No Insulation, No Leakage | [6 empty] | No Insulation, No Leakage | [5 empty] | No Insulation, No Leakage | [6 empty] | No Insulation, No Leakage | [6 empty] | No Insulation, No Leakage | [5 empty] | No Insulation, No Leakage | [6 empty] | No Insulation, No Leakage | [6 empty] | No Insulation, No Leakage
| Ambient | Square Feet of Floor Area | [5 empty] | Ambient | Square Feet of Floor Area | [5 empty] | Ambient | Square Feet of Floor Area | [10 empty] | Ambient | Square Feet of Floor Area | [5 empty] | Ambient |  | Square Feet of Floor Area | [11 empty] | Ambient | Square Feet of Floor Area |  |  |  |  | Ambient | Square Feet of Floor Area | [5 empty] | Ambient | Square Feet of Floor Area | [5 empty] | Ambient | Square Feet of Floor Area |  |  |  |  | Ambient | Square Feet of Floor Area | [5 empty] | Ambient | Square Feet of Floor Area | [5 empty] | Ambient | Square Feet of Floor Area |  |  |  |  | Ambient | Square Feet of Floor Area | [5 empty] | Ambient | Square Feet of Floor Area | [5 empty] | Ambient | Square Feet of Floor Area
| Dry Bulb | 3000 | 6000 | 9000 | 12000 | 15000 |  | Dry Bulb | 3000 | 6000 | 9000 | 12000 | 15000 |  | ∆ Grains ± | 3000 | 6000 | 9000 | 12000 | 15000 | [6 empty] | Dry Bulb | 3000 | 6000 | 9000 | 12000 | 15000 |  | Dry Bulb |  | 3000 |  | 6000 |  | 9000 |  | 12000 |  | 15000 |  |  |  | ∆ Grains ± | 3000 | 6000 | 9000 | 12000 | 15000 | Dry Bulb | 3000 | 6000 | 9000 | 12000 | 15000 |  | Dry Bulb | 3000 | 6000 | 9000 | 12000 | 15000 |  | ∆ Grains ± | 3000 | 6000 | 9000 | 12000 | 15000 | Dry Bulb | 3000 | 6000 | 9000 | 12000 | 15000 |  | Dry Bulb | 3000 | 6000 | 9000 | 12000 | 15000 |  | ∆ Grains ± | 3000 | 6000 | 9000 | 12000 | 15000 | Dry Bulb | 3000 | 6000 | 9000 | 12000 | 15000 |  | Dry Bulb | 3000 | 6000 | 9000 | 12000 | 15000 |  | ∆ Grains ± | 3000 | 6000 | 9000 | 12000 | 15000
| -10 | na | na | na | na | na |  | -10 | na | na | na | na | na |  | 10 | 0 | 0 | 0 | 0 | 0 | [6 empty] | -10 | na | na | na | na | na |  | -10 |  | na |  | na |  | na |  | na |  | na |  |  |  | 10 | 0 | 0 | 0 | 0 | 0 | -10 | na | na | na | na | na |  | -10 | na | na | na | na | na |  | 10 | 0 | 0 | 0 | 0 | 0 | -10 | na | na | na | na | na |  | -10 | na | na | na | na | na |  | 10 | 0 | 0 | 0 | 0 | 0 | -10 | na | na | na | na | na |  | -10 | na | na | na | na | na |  | 10 | 0 | 0 | 0 | 0 | 0
| 0 | na | na | na | na | na |  | 0 | na | na | na | na | na |  | 20 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | na | na | na | na | na |  | 0 |  | na |  | na |  | na |  | na |  | na |  |  |  | 20 | 0 | 0 | 0 | 0 | 0 | 0 | na | na | na | na | na |  | 0 | na | na | na | na | na |  | 20 | 0 | 0 | 0 | 0 | 0 | 0 | na | na | na | na | na |  | 0 | na | na | na | na | na |  | 20 | 0 | 0 | 0 | 0 | 0 | 0 | na | na | na | na | na |  | 0 | na | na | na | na | na |  | 20 | 0 | 0 | 0 | 0 | 0
| 10 | 0.057 | 0.063 | 0.069 | 0.075 | 0.081 |  | 10 | -0.0375 | -0.0405 | -0.0435 | -0.0465 | -0.0495 |  | 30 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 10 | 0.108 | 0.1185 | 0.129 | 0.1395 | 0.15 |  | 10 |  | -0.0645 |  | -0.07125 |  | -0.078 |  | -0.08475 |  | -0.0915 |  |  |  | 30 | 0 | 0 | 0 | 0 | 0 | 10 | 0.066 | 0.074625 | 0.08325 | 0.091875 | 0.1005 |  | 10 | -0.0435 | -0.047625 | -0.05175 | -0.055875 | -0.06 |  | 30 | 0 | 0 | 0 | 0 | 0 | 10 | 0.057 | 0.063 | 0.069 | 0.075 | 0.081 |  | 10 | -0.0375 | -0.0405 | -0.0435 | -0.0465 | -0.0495 |  | 30 | 0 | 0 | 0 | 0 | 0 | 10 | 0.0495 | 0.0555 | 0.0615 | 0.0675 | 0.0735 |  | 10 | -0.0315 | -0.0345 | -0.0375 | -0.0405 | -0.0435 |  | 30 | 0 | 0 | 0 | 0 | 0
| 20 | 0.051 | 0.05625 | 0.0615 | 0.06675 | 0.072 |  | 20 | -0.02925 | -0.0315 | -0.03375 | -0.036 | -0.03825 |  | 40 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 20 | 0.096 | 0.10538 | 0.11475 | 0.12413 | 0.1335 |  | 20 |  | -0.05025 |  | -0.0555 |  | -0.06075 |  | -0.066 |  | -0.07125 |  |  |  | 40 | 0 | 0 | 0 | 0 | 0 | 20 | 0.0585 | 0.066187 | 0.073875 | 0.081562 | 0.08925 |  | 20 | -0.03375 | -0.036937 | -0.040125 | -0.043312 | -0.0465 |  | 40 | 0 | 0 | 0 | 0 | 0 | 20 | 0.051 | 0.05625 | 0.0615 | 0.06675 | 0.072 |  | 20 | -0.02925 | -0.0315 | -0.03375 | -0.036 | -0.03825 |  | 40 | 0 | 0 | 0 | 0 | 0 | 20 | 0.04425 | 0.0495 | 0.05475 | 0.06 | 0.06525 |  | 20 | -0.02475 | -0.027 | -0.02925 | -0.0315 | -0.03375 |  | 40 | 0 | 0 | 0 | 0 | 0
| 30 | 0.045 | 0.0495 | 0.054 | 0.0585 | 0.063 |  | 30 | -0.021 | -0.0225 | -0.024 | -0.0255 | -0.027 |  | 50 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 30 | 0.084 | 0.09225 | 0.1005 | 0.10875 | 0.117 |  | 30 |  | -0.036 |  | -0.03975 |  | -0.0435 |  | -0.04725 |  | -0.051 |  |  |  | 50 | 0 | 0 | 0 | 0 | 0 | 30 | 0.051 | 0.05775 | 0.0645 | 0.07125 | 0.078 |  | 30 | -0.024 | -0.02625 | -0.0285 | -0.03075 | -0.033 |  | 50 | 0 | 0 | 0 | 0 | 0 | 30 | 0.045 | 0.0495 | 0.054 | 0.0585 | 0.063 |  | 30 | -0.021 | -0.0225 | -0.024 | -0.0255 | -0.027 |  | 50 | 0 | 0 | 0 | 0 | 0 | 30 | 0.039 | 0.0435 | 0.048 | 0.0525 | 0.057 |  | 30 | -0.018 | -0.0195 | -0.021 | -0.0225 | -0.024 |  | 50 | 0 | 0 | 0 | 0 | 0
| 40 | 0.039 | 0.04275 | 0.0465 | 0.05025 | 0.054 |  | 40 | -0.01275 | -0.0135 | -0.01425 | -0.015 | -0.01575 |  | 60 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 40 | 0.072 | 0.079125 | 0.08625 | 0.093375 | 0.1005 |  | 40 |  | -0.02175 |  | -0.024 |  | -0.02625 |  | -0.0285 |  | -0.03075 |  |  |  | 60 | 0 | 0 | 0 | 0 | 0 | 40 | 0.0435 | 0.049312 | 0.055125 | 0.060937 | 0.06675 |  | 40 | -0.01425 | -0.015562 | -0.016875 | -0.018187 | -0.0195 |  | 60 | 0 | 0 | 0 | 0 | 0 | 40 | 0.039 | 0.04275 | 0.0465 | 0.05025 | 0.054 |  | 40 | -0.01275 | -0.0135 | -0.01425 | -0.015 | -0.01575 |  | 60 | 0 | 0 | 0 | 0 | 0 | 40 | 0.03375 | 0.0375 | 0.04125 | 0.045 | 0.04875 |  | 40 | -0.01125 | -0.012 | -0.01275 | -0.0135 | -0.01425 |  | 60 | 0 | 0 | 0 | 0 | 0
| 50 | 0.033 | 0.036 | 0.039 | 0.042 | 0.045 |  | 50 | -0.0045 | -0.0045 | -0.0045 | -0.0045 | -0.0045 |  | 70 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 50 | 0.06 | 0.066 | 0.072 | 0.078 | 0.084 |  | 50 |  | -0.0075 |  | -0.00825 |  | -0.009 |  | -0.00975 |  | -0.0105 |  |  |  | 70 | 0 | 0 | 0 | 0 | 0 | 50 | 0.036 | 0.040875 | 0.04575 | 0.050625 | 0.0555 |  | 50 | -0.0045 | -0.004875 | -0.00525 | -0.005625 | -0.006 |  | 70 | 0 | 0 | 0 | 0 | 0 | 50 | 0.033 | 0.036 | 0.039 | 0.042 | 0.045 |  | 50 | -0.0045 | -0.0045 | -0.0045 | -0.0045 | -0.0045 |  | 70 | 0 | 0 | 0 | 0 | 0 | 50 | 0.0285 | 0.0315 | 0.0345 | 0.0375 | 0.0405 |  | 50 | -0.0045 | -0.0045 | -0.0045 | -0.0045 | -0.0045 |  | 70 | 0 | 0 | 0 | 0 | 0
| 60 | 0.027 | 0.02925 | 0.0315 | 0.03375 | 0.036 |  | 60 | 0.00375 | 0.0045 | 0.00525 | 0.006 | 0.00675 | [13 empty] | 60 | 0.048 | 0.052875 | 0.05775 | 0.062625 | 0.0675 |  | 60 |  | 0.00675 |  | 0.0075 |  | 0.00825 |  | 0.009 |  | 0.00975 |  |  |  | No leakage in supply duct, no load for return duct in conditioned space. | [5 empty] | 60 | 0.0285 | 0.032438 | 0.036375 | 0.040313 | 0.04425 |  | 60 | 0.00525 | 0.0058125 | 0.006375 | 0.0069375 | 0.0075 |  | No leakage in supply duct, no load for return duct in conditioned space. | [5 empty] | 60 | 0.027 | 0.02925 | 0.0315 | 0.03375 | 0.036 |  | 60 | 0.00375 | 0.0045 | 0.00525 | 0.006 | 0.00675 |  | No leakage in supply duct, no load for return duct in conditioned space. | [5 empty] | 60 | 0.02325 | 0.0255 | 0.02775 | 0.03 | 0.03225 |  | 60 | 0.00225 | 0.003 | 0.00375 | 0.0045 | 0.00525 |  | No leakage in supply duct, no load for return duct in conditioned space.
| 70 | 0.021 | 0.0225 | 0.024 | 0.0255 | 0.027 |  | 70 | 0.012 | 0.0135 | 0.015 | 0.0165 | 0.018 | [13 empty] | 70 | 0.036 | 0.03975 | 0.0435 | 0.04725 | 0.051 |  | 70 |  | 0.021 |  | 0.02325 |  | 0.0255 |  | 0.02775 |  | 0.03 | [9 empty] | 70 | 0.021 | 0.024 | 0.027 | 0.03 | 0.033 |  | 70 | 0.015 | 0.0165 | 0.018 | 0.0195 | 0.021 | [7 empty] | 70 | 0.021 | 0.0225 | 0.024 | 0.0255 | 0.027 |  | 70 | 0.012 | 0.0135 | 0.015 | 0.0165 | 0.018 | [7 empty] | 70 | 0.018 | 0.0195 | 0.021 | 0.0225 | 0.024 |  | 70 | 0.009 | 0.0105 | 0.012 | 0.0135 | 0.015
| 80 | 0.015 | 0.01575 | 0.0165 | 0.01725 | 0.018 |  | 80 | 0.02025 | 0.0225 | 0.02475 | 0.027 | 0.02925 |  | Leakage Correction (LCF) for Latent Gain | [11 empty] | 80 | 0.024 | 0.026625 | 0.02925 | 0.031875 | 0.0345 |  | 80 |  | 0.03525 |  | 0.039 |  | 0.04275 |  | 0.0465 |  | 0.05025 |  |  |  | Leakage Correction (LCF) for Latent Gain | [5 empty] | 80 | 0.0135 | 0.015563 | 0.017625 | 0.019688 | 0.02175 |  | 80 | 0.02475 | 0.027187 | 0.029625 | 0.032063 | 0.0345 |  | Leakage Correction (LCF) for Latent Gain | [5 empty] | 80 | 0.015 | 0.01575 | 0.0165 | 0.01725 | 0.018 |  | 80 | 0.02025 | 0.0225 | 0.02475 | 0.027 | 0.02925 |  | Leakage Correction (LCF) for Latent Gain | [5 empty] | 80 | 0.01275 | 0.0135 | 0.01425 | 0.015 | 0.01575 |  | 80 | 0.01575 | 0.018 | 0.02025 | 0.0225 | 0.02475 |  | Leakage Correction (LCF) for Latent Gain
[8 empty] | Ambient dry-bukb = (Summer design dry-bulb - Winter design dry-bulb) / 2 | 0 | 0 | 0 | 0 | 0 |  | Leakage | Any R-Value | [10 empty] | Ambient dry-bukb = (Summer design dry-bulb - Winter design dry-bulb) / 2 | [6 empty] | Ambient dry-bukb = (Summer design dry-bulb - Winter design dry-bulb) / 2 | [13 empty] | Leakage | Any R-Value |  |  |  |  | Ambient dry-bukb = (Summer design dry-bulb - Winter design dry-bulb) / 2 | [6 empty] | Ambient dry-bukb = (Summer design dry-bulb - Winter design dry-bulb) / 2 | [6 empty] | Leakage | Any R-Value |  |  |  |  | Ambient dry-bukb = (Summer design dry-bulb - Winter design dry-bulb) / 2 | [6 empty] | Ambient dry-bukb = (Summer design dry-bulb - Winter design dry-bulb) / 2 | [6 empty] | Leakage | Any R-Value |  |  |  |  | Ambient dry-bukb = (Summer design dry-bulb - Winter design dry-bulb) / 2 | [6 empty] | Ambient dry-bukb = (Summer design dry-bulb - Winter design dry-bulb) / 2 | [6 empty] | Leakage | Any R-Value
[15 empty] | 0.06 / 0.06 |  |  | na | [8 empty] | BHLF = (-3.750E-08 x Amb + 3.875E-06) x Floor Area - 1.088E-03 x Amb + 1.084E-01 | [6 empty] | BSGF = (5.000E-08 x Amb - 2.750E-06) x Floor Area + 1.275E-03 x Amb - 7.050E-02 | [13 empty] | 0.06 / 0.06 |  |  | na |  |  | BHLF = (-3.125E-08 x Amb + 3.188E-06) x Floor Area - 6.563E-04 x Amb + 6.394E-02 | [6 empty] | BSGF = (3.125E-08 x Amb - 1.688E-06) x Floor Area + 8.813E-04 x Amb - 4.819E-02 | [6 empty] | 0.06 / 0.06 |  |  | na |  |  | BHLF = (-2.500E-08 x Amb + 2.250E-06) x Floor Area - 5.250E-04 x Amb + 5.625E-02 | [6 empty] | BSGF = (2.500E-08 x Amb - 1.125E-06) x Floor Area + 7.500E-04 x Amb - 4.200E-02 | [6 empty] | 0.06 / 0.06 |  |  | na |  |  | BHLF = (-2.500E-08 x Amb + 2.250E-06) x Floor Area - 4.500E-04 x Amb + 4.800E-02 | [6 empty] | BSGF = (2.500E-08 x Amb - 1.250E-06) x Floor Area + 6.000E-04 x Amb - 3.450E-02 | [6 empty] | 0.06 / 0.06 |  |  | na
| 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.09 / 0.15 |  |  | na | [8 empty] | R-Value Correction |  | R0 | R2 | R4 | R6 |  | R-Value Correction |  |  |  | R0 |  | R2 |  | R4 |  | R6 |  |  |  | 0.09 / 0.15 |  |  | na | [16 empty] | 0.09 / 0.15 |  |  | na | [16 empty] | 0.09 / 0.15 |  |  | na | [16 empty] | 0.09 / 0.15 |  |  | na
| 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.12 / 0.24 |  |  | na | [8 empty] | (WIF - Heat Loss) |  | 1 | 0.33 | 0.2 | 0.14 |  | (WIF - Sensible Gain) |  |  |  | 1 |  | 0.33 |  | 0.2 |  | 0.14 |  |  |  | 0.12 / 0.24 |  |  | na | [16 empty] | 0.12 / 0.24 |  |  | na | [16 empty] | 0.12 / 0.24 |  |  | na | [16 empty] | 0.12 / 0.24 |  |  | na
[15 empty] | 0.24 / 0.47 |  |  | na | [29 empty] | 0.24 / 0.47 |  |  | na |  |  | R-Value Correction |  | R0 | R2 | R4 | R6 |  | R-Value Correction |  | R0 | R2 | R4 | R6 |  | 0.24 / 0.47 |  |  | na |  |  | R-Value Correction |  | R0 | R2 | R4 | R6 |  | R-Value Correction |  | R0 | R2 | R4 | R6 |  | 0.24 / 0.47 |  |  | na |  |  | R-Value Correction |  | R0 | R2 | R4 | R6 |  | R-Value Correction |  | R0 | R2 | R4 | R6 |  | 0.24 / 0.47 |  |  | na
[15 empty] | 0.35 / 0.70 |  |  | na | [29 empty] | 0.35 / 0.70 |  |  | na |  |  | (WIF - Heat Loss) |  | 1 | 0.33 | 0.2 | 0.14 |  | (WIF - Sensible Gain) |  | 1 | 0.33 | 0.2 | 0.14 |  | 0.35 / 0.70 |  |  | na |  |  | (WIF - Heat Loss) |  | 1 | 0.33 | 0.2 | 0.14 |  | (WIF - Sensible Gain) |  | 1 | 0.33 | 0.2 | 0.14 |  | 0.35 / 0.70 |  |  | na |  |  | (WIF - Heat Loss) |  | 1 | 0.33 | 0.2 | 0.14 |  | (WIF - Sensible Gain) |  | 1 | 0.33 | 0.2 | 0.14 |  | 0.35 / 0.70 |  |  | na
[27 empty] | Leakage Correction (LCF) for Heat Loss | [6 empty] | Leakage Correction (LCF) for Sensible Gain
[27 empty] | Leakage | R0 | R2 | R4 | R6 |  |  | Leakage |  | R0 |  | R2 |  | R4 |  | R6
| Leakage Correction (LCF) for Heat Loss | [6 empty] | Leakage Correction (LCF) for Sensible Gain | [18 empty] | 0.06 / 0.06 | 1 | 1 | 1 | 1 |  |  | 0.06 / 0.06 |  | 1 |  | 1 |  | 1 |  | 1 | [5 empty] | Surface Area Adjustment (LGA) for Latent Gain | [5 empty] | Leakage Correction (LCF) for Heat Loss | [6 empty] | Leakage Correction (LCF) for Sensible Gain | [6 empty] | Surface Area Adjustment (LGA) for Latent Gain | [5 empty] | Leakage Correction (LCF) for Heat Loss | [6 empty] | Leakage Correction (LCF) for Sensible Gain | [6 empty] | Surface Area Adjustment (LGA) for Latent Gain | [5 empty] | Leakage Correction (LCF) for Heat Loss | [6 empty] | Leakage Correction (LCF) for Sensible Gain | [6 empty] | Surface Area Adjustment (LGA) for Latent Gain
| Leakage | R0 | R2 | R4 | R6 |  |  | Leakage | R0 | R2 | R4 | R6 | [14 empty] | 0.09 / 0.15 | 1 | 1 | 1 | 1 |  |  | 0.09 / 0.15 |  | 1 |  | 1 |  | 1 |  | 1 | [5 empty] | Return side LGA = Actual return-side area / Default return-side area | [5 empty] | Leakage | R0 | R2 | R4 | R6 |  |  | Leakage | R0 | R2 | R4 | R6 |  |  | Return side LGA = Actual return-side area / Default return-side area | [5 empty] | Leakage | R0 | R2 | R4 | R6 |  |  | Leakage | R0 | R2 | R4 | R6 |  |  | Return side LGA = Actual return-side area / Default return-side area | [5 empty] | Leakage | R0 | R2 | R4 | R6 |  |  | Leakage | R0 | R2 | R4 | R6 |  |  | Return side LGA = Actual return-side area / Default return-side area
| 0.06 / 0.06 | 1 | 1 | 1 | 1 |  |  | 0.06 / 0.06 | 1 | 1 | 1 | 1 | [14 empty] | 0.12 / 0.24 | 1 | 1 | 1 | 1 |  |  | 0.12 / 0.24 |  | 1 |  | 1 |  | 1 |  | 1 | [11 empty] | 0.06 / 0.06 | 1 | 1 | 1 | 1 |  |  | 0.06 / 0.06 | 1 | 1 | 1 | 1 | [8 empty] | 0.06 / 0.06 | 1 | 1 | 1 | 1 |  |  | 0.06 / 0.06 | 1 | 1 | 1 | 1 | [8 empty] | 0.06 / 0.06 | 1 | 1 | 1 | 1 |  |  | 0.06 / 0.06 | 1 | 1 | 1 | 1
| 0.09 / 0.15 | 1 | 1 | 1 | 1 |  |  | 0.09 / 0.15 | 1 | 1 | 1 | 1 | [14 empty] | 0.24 / 0.47 | 1 | 1 | 1 | 1 |  |  | 0.24 / 0.47 |  | 1 |  | 1 |  | 1 |  | 1 | [5 empty] | Procedure for Latent Gain Adjustment | [5 empty] | 0.09 / 0.15 | 1 | 1 | 1 | 1 |  |  | 0.09 / 0.15 | 1 | 1 | 1 | 1 |  |  | Procedure for Latent Gain Adjustment | [5 empty] | 0.09 / 0.15 | 1 | 1 | 1 | 1 |  |  | 0.09 / 0.15 | 1 | 1 | 1 | 1 |  |  | Procedure for Latent Gain Adjustment | [5 empty] | 0.09 / 0.15 | 1 | 1 | 1 | 1 |  |  | 0.09 / 0.15 | 1 | 1 | 1 | 1 |  |  | Procedure for Latent Gain Adjustment
| 0.12 / 0.24 | 1 | 1 | 1 | 1 |  |  | 0.12 / 0.24 | 1 | 1 | 1 | 1 | [14 empty] | 0.35 / 0.70 | 1 | 1 | 1 | 1 |  |  | 0.35 / 0.70 |  | 1 |  | 1 |  | 1 |  | 1 | [5 empty] | Step 1: Select the base case latent gain value (multiply by - 1.0 for negative Grains). | [5 empty] | 0.12 / 0.24 | 1 | 1 | 1 | 1 |  |  | 0.12 / 0.24 | 1 | 1 | 1 | 1 |  |  | Step 1: Select the base case latent gain value (multiply by - 1.0 for negative Grains). | [5 empty] | 0.12 / 0.24 | 1 | 1 | 1 | 1 |  |  | 0.12 / 0.24 | 1 | 1 | 1 | 1 |  |  | Step 1: Select the base case latent gain value (multiply by - 1.0 for negative Grains). | [5 empty] | 0.12 / 0.24 | 1 | 1 | 1 | 1 |  |  | 0.12 / 0.24 | 1 | 1 | 1 | 1 |  |  | Step 1: Select the base case latent gain value (multiply by - 1.0 for negative Grains).
| 0.24 / 0.47 | 1 | 1 | 1 | 1 |  |  | 0.24 / 0.47 | 1 | 1 | 1 | 1 | [35 empty] | Step 2: Apply leakage correction to the Step 1 value. | [5 empty] | 0.24 / 0.47 | 1 | 1 | 1 | 1 |  |  | 0.24 / 0.47 | 1 | 1 | 1 | 1 |  |  | Step 2: Apply leakage correction to the Step 1 value. | [5 empty] | 0.24 / 0.47 | 1 | 1 | 1 | 1 |  |  | 0.24 / 0.47 | 1 | 1 | 1 | 1 |  |  | Step 2: Apply leakage correction to the Step 1 value. | [5 empty] | 0.24 / 0.47 | 1 | 1 | 1 | 1 |  |  | 0.24 / 0.47 | 1 | 1 | 1 | 1 |  |  | Step 2: Apply leakage correction to the Step 1 value.
| 0.35 / 0.70 | 1 | 1 | 1 | 1 |  |  | 0.35 / 0.70 | 1 | 1 | 1 | 1 | [35 empty] | Step 3: Apply surface area adjustment to the Step 2 value. | [5 empty] | 0.35 / 0.70 | 1 | 1 | 1 | 1 |  |  | 0.35 / 0.70 | 1 | 1 | 1 | 1 |  |  | Step 3: Apply surface area adjustment to the Step 2 value. | [5 empty] | 0.35 / 0.70 | 1 | 1 | 1 | 1 |  |  | 0.35 / 0.70 | 1 | 1 | 1 | 1 |  |  | Step 3: Apply surface area adjustment to the Step 2 value. | [5 empty] | 0.35 / 0.70 | 1 | 1 | 1 | 1 |  |  | 0.35 / 0.70 | 1 | 1 | 1 | 1 |  |  | Step 3: Apply surface area adjustment to the Step 2 value.
[27 empty] | Default Duct Wall Surface Area (SqFt) | [12 empty] | Surface Area Factors
[40 empty] | Leakage |  | Ks |  | Kr
| Default Duct Wall Surface Area (SqFt) | [9 empty] | Surface Area Factors | [15 empty] | Floor Area Look-Up Value | [12 empty] | 0.06 / 0.06 |  | 1 |  | 0 | [9 empty] | Default Duct Wall Surface Area (SqFt) | [9 empty] | Surface Area Factors | [9 empty] | Default Duct Wall Surface Area (SqFt) | [9 empty] | Surface Area Factors | [9 empty] | Default Duct Wall Surface Area (SqFt) | [9 empty] | Surface Area Factors
[11 empty] | Leakage | Ks | Kr | [13 empty] | 3,000 SqFt |  | 6,000 SqFt |  | 9,000 SqFt |  | 12,000 SqFt |  |  | 15,000 SqFt |  |  |  | 0.09 / 0.15 |  | 1 |  | 0 | [19 empty] | Leakage | Ks | Kr | [17 empty] | Leakage | Ks | Kr | [17 empty] | Leakage | Ks | Kr
| Floor Area Look-Up Value | [9 empty] | 0.06 / 0.06 | 1 | 0 | [13 empty] | Supply | Return | Supply | Return | Supply | Return | Supply | Return |  | Supply |  | Return |  | 0.12 / 0.24 |  | 1 |  | 0 | [9 empty] | Floor Area Look-Up Value | [9 empty] | 0.06 / 0.06 | 1 | 0 | [7 empty] | Floor Area Look-Up Value | [9 empty] | 0.06 / 0.06 | 1 | 0 | [7 empty] | Floor Area Look-Up Value | [9 empty] | 0.06 / 0.06 | 1 | 0
| 3000 | 3000 | 6000 | 6000 | 9000 | 9000 | 12000 | 12000 | 15000 | 15000 | 0.09 / 0.15 | 1 | 0 | [13 empty] | 634 | 0 | 1399 | 0 | 2143 | 0 | 2988 | 0 |  | 4533 |  | 0 |  | 0.24 / 0.47 |  | 1 |  | 0 | [9 empty] | 3,000 SqFt |  | 6,000 SqFt |  | 9,000 SqFt |  | 12,000 SqFt |  | 15,000 SqFt |  | 0.09 / 0.15 | 1 | 0 | [7 empty] | 3,000 SqFt |  | 6,000 SqFt |  | 9,000 SqFt |  | 12,000 SqFt |  | 15,000 SqFt |  | 0.09 / 0.15 | 1 | 0 | [7 empty] | 3,000 SqFt |  | 6,000 SqFt |  | 9,000 SqFt |  | 12,000 SqFt |  | 15,000 SqFt |  | 0.09 / 0.15 | 1 | 0
| Supply | Return | Supply | Return | Supply | Return | Supply | Return | Supply | Return | 0.12 / 0.24 | 1 | 0 | [13 empty] | See Section 9-9 for instruction for determining the floor area look-up value. | [12 empty] | 0.35 / 0.70 |  | 1 |  | 0 | [9 empty] | Supply | Return | Supply | Return | Supply | Return | Supply | Return | Supply | Return | 0.12 / 0.24 | 1 | 0 | [7 empty] | Supply | Return | Supply | Return | Supply | Return | Supply | Return | Supply | Return | 0.12 / 0.24 | 1 | 0 | [7 empty] | Supply | Return | Supply | Return | Supply | Return | Supply | Return | Supply | Return | 0.12 / 0.24 | 1 | 0
| 1017 | 0 | 2333 | 0 | 3574 | 0 | 5475 | 0 | 7128 | 0 | 0.24 / 0.47 | 1 | 0 | [40 empty] | 764 | 0 | 1866 | 0 | 3212 | 0 | 4479 | 0 | 5832 | 0 | 0.24 / 0.47 | 1 | 0 | [7 empty] | 1017 | 0 | 2333 | 0 | 3574 | 0 | 5475 | 0 | 7128 | 0 | 0.24 / 0.47 | 1 | 0 | [7 empty] | 1144 | 0 | 2568 | 0 | 4287 | 0 | 6469 | 0 | 8423 | 0 | 0.24 / 0.47 | 1 | 0
[11 empty] | 0.35 / 0.70 | 1 | 0 | [40 empty] | See Section 9-9 for instruction for determining the floor area look-up value. | [9 empty] | 0.35 / 0.70 | 1 | 0 | [7 empty] | See Section 9-9 for instruction for determining the floor area look-up value. | [9 empty] | 0.35 / 0.70 | 1 | 0 | [7 empty] | See Section 9-9 for instruction for determining the floor area look-up value. | [9 empty] | 0.35 / 0.70 | 1 | 0

## Wrk G (hidden)
[17 empty] | Scroll for space 3 and 4 >>> | [11 empty] | Scroll for space 4 >>>
Space |  |  | Worksheet G | [7 empty] | Space |  |  | Worksheet G | [7 empty] | Space |  |  | Worksheet G | [7 empty] | Space |  |  | Worksheet G
1 |  |  | For Duct Runs in Unconditioned Space | [7 empty] | 2 |  |  | For Duct Runs in Unconditioned Space | [7 empty] | 3 |  |  | For Duct Runs in Unconditioned Space | [7 empty] | 4 |  |  | For Duct Runs in Unconditioned Space
|  |  | Type of space load: | #NAME? | Month: | Jul & Aug | Hour: | 15:00 | [5 empty] | Type of space load: | #NAME? | Month: | Jul & Aug | Hour: | 0.625 | [5 empty] | Type of space load: | #NAME? | Month: | Jul & Aug | Hour: | 0.625 | [5 empty] | Type of space load: | #NAME? | Month: | Jul & Aug | Hour: | 0.625
Location of duct runs: | [8 empty] | Levels served by duct runs (1, 2 or 3) | One | Location of duct runs: | [8 empty] | Levels served by duct runs (1, 2 or 3) |  | Location of duct runs: | [8 empty] | Levels served by duct runs (1, 2 or 3) |  | Location of duct runs: | [8 empty] | Levels served by duct runs (1, 2 or 3)
Percent duct system surface area in space |  |  |  | 100 | 100 |  |  |  | Floor area of primary level (SqFt) | 1117 | Percent duct system surface area in space | [8 empty] | Floor area of primary level (SqFt) |  | Percent duct system surface area in space | [8 empty] | Floor area of primary level (SqFt) |  | Percent duct system surface area in space | [8 empty] | Floor area of primary level (SqFt)
Airway shape and configuration | [8 empty] | Floor areas of second and third levels (SqFt) |  | Airway shape and configuration | [8 empty] | Floor areas of second and third levels (SqFt) |  | Airway shape and configuration | [8 empty] | Floor areas of second and third levels (SqFt) |  | Airway shape and configuration | [8 empty] | Floor areas of second and third levels (SqFt)
Duct | Config. | Look Up | FA1 / FA2 | Floor Area | DF ALF | Ambient db | DF ALF | ALF for | Ambient db | Amb Grains | Duct | Config. | Look Up | FA1 / FA2 | Floor Area | ALF | Ambient db | DF ALF | ALF for | Ambient db | Amb Grains | Duct | Config. | Look Up | FA1 / FA2 | Floor Area | ALF | DF ALF | ALF for | ALF | Ambient db | Amb Grains | Duct | Config. | Look Up | FA1 / FA2 | Floor Area | ALF | Ambient db | DF ALF | ALF for | Ambient db | Amb Grains
Table | Case | Area SqFt |  | for ALF | for Heating | for Heating | for Cooling | Duct Table | for Cooling | for Cooling | Table | Case | Area SqFt |  | for ALF | for Heating | for Heating | for Cooling | Duct Tbl | for Cooling | for Cooling | Table | Case | Area SqFt |  | for ALF | for Heating | for Cooling | Duct Tbl | for Cooling | for Cooling | for Cooling | Table | Case | Area SqFt |  | for ALF | for Heating | for Heating | for Cooling | Duct Tbl | for Cooling | for Cooling
#N/A | 1 | 1117 | 1 | 1117 | 0.36916 | 0 | 1.6412 | 1.5 | 0 | 3 |  |  | 0 | 1 | 0 | 0.36916 |  | 1.6412 | [5 empty] | 0 | 1 | 0 | 0.36916 |  | 1.6412 | [5 empty] | 0 | 1 | 0 | 0.36916 |  | 1.6412
|  | ▲ If 999999 or #VALUE, there is an error in floor area data; see cells L6 and L7. | [10 empty] | ▲ If 999999 or #VALUE, there is an error in floor area data; see cells L6 and L7. | [10 empty] | ▲ If 999999 or #VALUE, there is an error in floor area data; see cells L6 and L7. | [10 empty] | ▲ If 999999 or #VALUE, there is an error in floor area data; see cells L6 and L7.
* Refer to Section 9.9 for guidance pertaining to case number and look-up floor area. See Section 9.7 for heating SAT. | [10 empty] | * Refer to Section 9.9 for guidance pertaining to case number and look-up floor area. See Section 9.7 for heating SAT. | [10 empty] | * Refer to Section 9.9 for guidance pertaining to case number and look-up floor area. See Section 9.7 for heating SAT. | [10 empty] | * Refer to Section 9.9 for guidance pertaining to case number and look-up floor area. See Section 9.7 for heating SAT.
* For ambient conditions, see the Tbl 7-AMB tab. | [10 empty] | * For ambient conditions, see the Tbl 7-AMB tab. | [10 empty] | * For ambient conditions, see the Tbl 7-AMB tab. | [10 empty] | * For ambient conditions, see the Tbl 7-AMB tab.
* Default ALF for heating and cooling = Sensible load from line 14 of Form N1 / (FA x 1.1 x ACF x ∆T) where: ∆T = SAR or SAD | [10 empty] | * Default ALF for heating and cooling = Sensible load from line 14 of Form N1 / (FA x 1.1 x ACF x ∆T) where: ∆T = SAR or SAD | [10 empty] | * Default ALF for heating and cooling = Sensible load from line 14 of Form N1 / (FA x 1.1 x ACF x ∆T) where: ∆T = SAR or SAD | [10 empty] | * Default ALF for heating and cooling = Sensible load from line 14 of Form N1 / (FA x 1.1 x ACF x ∆T) where: ∆T = SAR or SAD
* The ALF for the duct table equals the default ALF for the peak load month and hour or a value specified by the practitioner. | [10 empty] | * The ALF for the duct table equals the default ALF for the peak load month and hour or a value specified by the practitioner. | [10 empty] | * The ALF for the duct table equals the default ALF or a value specified by the practitioner. | [10 empty] | * The ALF for the duct table equals the default ALF for the peak load month and hour or a value specified by the practitioner.
* If the cooling Cfm is used year around, the heating ALF equals the cooling ALF. | [10 empty] | * If the cooling Cfm is used year around, the heating ALF equals the cooling ALF. | [10 empty] | * If the cooling Cfm is used year around, the heating ALF equals the cooling ALF. | [10 empty] | * If the cooling Cfm is used year around, the heating ALF equals the cooling ALF.
* For duct routed through multiple locations, use Worksheet G for Space 2; Space 3 and Space 4 (see also, Section 9.16) | [10 empty] | * For duct routed through multiple locations, use Worksheet G for Space 2; Space 3 and Space 4 (see also, Section 9.16) | [10 empty] | * For duct routed through multiple locations, use Worksheet G for Space 2; Space 3 and Space 4 (see also, Section 9.16) | [10 empty] | * For duct routed through multiple locations, use Worksheet G for Space 2; Space 3 and Space 4 (see also, Section 9.16)
Sidebar calc for look-up floor area. |  |  |  |  | Line 14 loads on Form N1 |  | ACF | AHR | AHD |  | Sidebar calc for look-up floor area. |  |  |  |  | Line 14 loads on Form N1 |  | ACF | AHR | AHD |  | Sidebar calc for look-up floor area. |  |  |  |  | Line 14 loads on Form N1 |  | ACF | AHR | AHD |  | Sidebar calc for look-up floor area. |  |  |  |  | Line 14 loads on Form N1 |  | ACF | AHR | AHD
Large/Small | Large+Small | 0.75 x (L + S) | Case 1 | Case 2 or 3 | Heating | Cooling |  | °F | °F |  | Large/Small | Large+Small | 0.75 x (L + S) | Case 1 | Case 2 or 3 | Heating | Cooling |  | °F | °F |  | Large/Small | Large+Small | 0.75 x (L + S) | Case 1 | Case 2 or 3 | Heating | Cooling |  | °F | °F |  | Large/Small | Large+Small | 0.75 x (L + S) | Case 1 | Case 2 or 3 | Heating | Cooling |  | °F | °F
1 | 1117 | 837.75 | 1117 | 0 | 13607.5758 | 40332.0407 | 1 | 30 | 20 |  | 1 | FALSE | 0 | 0 | 0 |  |  | 1 | 30 | 20 |  | 1 | FALSE | 0 | 0 | 0 |  |  | 1 | 30 | 20 |  | 1 | FALSE | 0 | 0 | 0 |  |  | 1 | 30 | 20
ALF = Line 14 Load / (FA x 1.1 x ACF x TD) |  |  |  |  | Indoor Temps Heating |  |  | Indoor Temps Cooling |  |  | ALF = Line 14 Load / (FA x 1.1 x ACF x TD) |  |  |  |  | Indoor Temps Heating |  |  | Indoor Temps Cooling |  |  | ALF = Line 14 Load / (FA x 1.1 x ACF x TD) |  |  |  |  | Indoor Temps Heating |  |  | Indoor Temps Cooling |  |  | ALF = Line 14 Load / (FA x 1.1 x ACF x TD) |  |  |  |  | Indoor Temps Heating |  |  | Indoor Temps Cooling
Where: The load is Btuh of heating or sensible cooling and FA is the floor area of the space. |  |  |  |  | SAT | IAT |  | IAT | SAT |  | Where: The load is Btuh of heating or sensible cooling and FA is the floor area of the space. |  |  |  |  | SAT | IAT |  | IAT | SAT |  | Where: The load is Btuh of heating or sensible cooling and FA is the floor area of the space. |  |  |  |  | SAT | IAT |  | IAT | SAT |  | Where: The load is Btuh of heating or sensible cooling and FA is the floor area of the space. |  |  |  |  | SAT | IAT |  | IAT | SAT
[5 empty] | 100 | 70 |  | 75 | 55 | [6 empty] | 100 | 70 |  | 75 | 55 | [6 empty] | 100 | 70 |  | 75 | 55 | [6 empty] | 100 | 70 |  | 75 | 55
Part 1) Enter base-case load factors and latent heat value from Table 7 | [6 empty] | Side bar interpolation engine |  |  |  | Part 1) Enter base-case load factors and latent heat value from Table 7 (eyeball interpolation is acceptable) | [10 empty] | Part 1) Enter base-case load factors and latent heat value from Table 7 (eyeball interpolation is acceptable) | [10 empty] | Part 1) Enter base-case load factors and latent heat value from Table 7 (eyeball interpolation is acceptable)
| R-Value |  |  |  | Base-case factors from table |  | Table value | Floor SF 1 | Floor SF 2 | SF Actual |  | R-Value |  |  |  | Base-case factors from table | [6 empty] | R-Value |  |  |  | Base-case factors from table | [6 empty] | R-Value |  |  |  | Base-case factors from table
1 | 0 |  |  | BHLF = | #N/A |  | °F or Gr | 3000 | 6000 | 3834 | 1 |  |  |  | BHLF = | [6 empty] | 1 |  |  |  | BHLF = | [6 empty] | 1 |  |  |  | BHLF =
2 | Leakage |  |  | BSGF = | #N/A |  | 30 | 1808 | 3942 | 2401.252 | 2 | Leakage |  |  | BSGF = | [6 empty] | 2 | Leakage |  |  | BSGF = | [6 empty] | 2 | Leakage |  |  | BSGF =
3 | #N/A |  |  | BLG (Btuh) = | #N/A |  | 40 | 2307 | 5027 | 3063.16 | 3 |  |  |  | BLG (Btuh) = | [6 empty] | 3 |  |  |  | BLG (Btuh) = | [6 empty] | 3 |  |  |  | BLG (Btuh) =
Part 2) R-Value Correction (WIF) | [6 empty] | Actual °F or Gr |  |  |  | Part 2) R-Value Correction (WIF) | [10 empty] | Part 2) R-Value Correction (WIF) | [10 empty] | Part 2) R-Value Correction (WIF)
[7 empty] | 35 |  | Load Factor or Gr = | 2732.206
4 |  |  |  | WIFloss = | #N/A | [5 empty] | 4 |  |  |  | WIFloss = | [6 empty] | 4 |  |  |  | WIFloss = | [6 empty] | 4 |  |  |  | WIFloss =
5 |  |  |  | WIFgain = | #N/A |  |  | Floor SF 1 | Floor SF 2 | SF Interp | 5 |  |  |  | WIFgain = | [6 empty] | 5 |  |  |  | WIFgain = | [6 empty] | 5 |  |  |  | WIFgain =
Part 3) Leakage Rate Correction (LCF) | [6 empty] | DF Duct SqFt | 646 | 1397 | 854.778 | Part 3) Leakage Rate Correction (LCF) | [10 empty] | Part 3) Leakage Rate Correction (LCF) | [10 empty] | Part 3) Leakage Rate Correction (LCF)
6 |  |  |  | LCFloss = | #N/A |  |  |  |  | SF Extrap | 6 |  |  |  | LCFloss = | [6 empty] | 6 |  |  |  | LCFloss = | [6 empty] | 6 |  |  |  | LCFloss =
7 |  |  |  | LCFgain = | #N/A |  |  |  |  | 0 | 7 |  |  |  | LCFgain = | [6 empty] | 7 |  |  |  | LCFgain = | [6 empty] | 7 |  |  |  | LCFgain =
8 |  |  |  | LCFlatent = | #N/A | [5 empty] | 8 |  |  |  | LCFlatent = | [6 empty] | 8 |  |  |  | LCFlatent = | [6 empty] | 8 |  |  |  | LCFlatent =
Part 4) Surface Area Adjustment | [10 empty] | Part 4) Surface Area Adjustment | [10 empty] | Part 4) Surface Area Adjustment | [10 empty] | Part 4) Surface Area Adjustment
[5 empty] | Supply-Side |  |  |  |  | Return-Side | [5 empty] | Supply-Side |  |  |  |  | Return-Side | [5 empty] | Supply-Side |  |  |  |  | Return-Side | [5 empty] | Supply-Side |  |  |  |  | Return-Side
9 |  |  |  | Ks = | #N/A |  |  |  | Kr = | #N/A | 9 |  |  |  | Ks = |  |  |  |  | Kr = | 1 | 9 |  |  |  | Ks = |  |  |  |  | Kr = | 1 | 9 |  |  |  | Ks = |  |  |  |  | Kr = | 1
10 |  |  |  | Installed or default supply area (SqFt) = | #N/A |  |  |  | Installed or default return area (SqFt) = | #N/A | 10 |  |  |  | Installed or default supply area (SqFt) = |  |  |  |  | Installed or default return area (SqFt) = |  | 10 |  |  |  | Installed or default supply area (SqFt) = |  |  |  |  | Installed or default return area (SqFt) = |  | 10 |  |  |  | Installed or default supply area (SqFt) = |  |  |  |  | Installed or default return area (SqFt) =
11 |  |  |  | Default supply area (SqFt) = | #N/A |  |  |  | Default return area (SqFt) = | #N/A | 11 |  |  |  | Default supply area (SqFt) = |  |  |  |  | Default return area (SqFt) = |  | 11 |  |  |  | Default supply area (SqFt) = |  |  |  |  | Default return area (SqFt) = |  | 11 |  |  |  | Default supply area (SqFt) = |  |  |  |  | Default return area (SqFt) =
12 |  |  |  | Rs = Installed area / default area = | #N/A |  |  |  | Rr = Installed area / default area = | #N/A | 12 |  |  |  | Rs = Installed area / default area = | 1 |  |  |  | Rr = Installed area / default area = | 1 | 12 |  |  |  | Rs = Installed area / default area = | 1 |  |  |  | Rr = Installed area / default area = | 1 | 12 |  |  |  | Rs = Installed area / default area = | 1 |  |  |  | Rr = Installed area / default area = | 1
Part 5) Effective Loss and Gain Factors | [10 empty] | Part 5) Effective Loss and Gain Factors | [10 empty] | Part 5) Effective Loss and Gain Factors | [10 empty] | Part 5) Effective Loss and Gain Factors
|  |  |  | To Form N1 > | Line 14a |  |  |  | To Form N1 > | Line 15 |  |  |  |  | To Form N1 > | Line 14a |  |  |  | To Form N1 > | Line 15 |  |  |  |  | To Form N1 > | Line 14a |  |  |  | To Form N1 > | Line 15 |  |  |  |  | To Form N1 > | Line 14a |  |  |  | To Form N1 > | Line 15
13 |  |  |  | EHLF = BHLF x WIFloss x LFCloss x Ks x Rs = | #N/A |  |  |  | EHLF = BHLF x WIFloss x LFCloss x Kr x Rr = | #N/A | 13 |  |  |  | EHLF = BHLF x WIFloss x LFCloss x Ks x Rs = | 0 |  |  |  | EHLF = BHLF x WIFloss x LFCloss x Kr x Rr = | 0 | 13 |  |  |  | EHLF = BHLF x WIFloss x LFCloss x Ks x Rs = | 0 |  |  |  | EHLF = BHLF x WIFloss x LFCloss x Kr x Rr = | 0 | 13 |  |  |  | EHLF = BHLF x WIFloss x LFCloss x Ks x Rs = | 0 |  |  |  | EHLF = BHLF x WIFloss x LFCloss x Kr x Rr = | 0
14 |  |  |  | ESGF = BSFG x WIFgain x LCFgain x Ks x Rs = | #N/A |  |  |  | ESGF = BSFG x WIFgain x LCFgain x Kr x Rr = | #N/A | 14 |  |  |  | ESGF = BSFG x WIFgain x LCFgain x Ks x Rs = | 0 |  |  |  | ESGF = BSFG x WIFgain x LCFgain x Kr x Rr = | 0 | 14 |  |  |  | ESGF = BSFG x WIFgain x LCFgain x Ks x Rs = | 0 |  |  |  | ESGF = BSFG x WIFgain x LCFgain x Kr x Rr = | 0 | 14 |  |  |  | ESGF = BSFG x WIFgain x LCFgain x Ks x Rs = | 0 |  |  |  | ESGF = BSFG x WIFgain x LCFgain x Kr x Rr = | 0
15 | [8 empty] | ELG (Btuh) = BLG x LCFlatent x Rr = | #N/A | 15 | [8 empty] | ELG (Btuh) = BLG x LCFlatent x Rr = | 0 | 15 | [8 empty] | ELG (Btuh) = BLG x LCFlatent x Rr = | 0 | 15 | [8 empty] | ELG (Btuh) = BLG x LCFlatent x Rr = | 0
[6 empty] | Note: EHLF, ESGF and ELG are zero for a return air ceiling plenum. Use Worksheet RAP-1 or RAP-2 to evaluate the return air load for heating and sensible cooling. | [10 empty] | Note: EHLF, ESGF and ELG are zero for a return air ceiling plenum. Use Worksheet RAP-1 or RAP-2 to evaluate the return air load for heating and sensible cooling. | [10 empty] | Note: EHLF, ESGF and ELG are zero for a return air ceiling plenum. Use Worksheet RAP-1 or RAP-2 to evaluate the return air load for heating and sensible cooling. | [10 empty] | Note: EHLF, ESGF and ELG are zero for a return air ceiling plenum. Use Worksheet RAP-1 or RAP-2 to evaluate the return air load for heating and sensible cooling.
Note on G9: ALF for sapce load in cell G19.
Note on I9: ALF for sapce load in cell H19.
Note on J9: ALF for peak space load on air handler.
Note on U9: ALF for sapce load in cell H19.
Note on V9: Air loading factor for peak sapce load on air handler.
Note on AF9: ALF for sapce load in cell H19.
Note on AG9: Air loading factor for peak sapce load on air handler.
Note on AS9: ALF for sapce load in cell H19.
Note on AT9: Air loading factor for peak sapce load on air handler.

## VentilationI
Ventilation
Value
0
CFM / Person
|  | 0 |  | 63
CFM
| 689 | 689 | 3 | 689
►Return to N1 Form
Air Changes/Hour
Occupants
Code CFM

## Notes
Release Notes:
Version N5ae 1.00 30JAN08 | Initial Release
Version N5ae 1.01 29MAR08 | Fixed duct error for square feet less than 3000
Fixed lookup for table cities on Form N1
Fixed shaded glass calculations
Version N5ae 1.02 09JUL08 | Fixed ommission of glass HTM on Form N1
Version N5ae 1.03 24AUG08 | Fixed tilt angle entry of zero for horizontal skylights
Version N5ae 1.04 04NOV08 | Fixed blower selection bug
Fixed Btuh gain for lights
Added door infiltration Tables 5F & 5G to infiltration calculation
Version N5ae 1.05 04FEB09 | Added skylight curb and shaft data input
Version N5ae 1.06 27APR09 | Fixed Btuh gain for food service equipment and investigated loads calculation
Added Comments Tab
Version N5ae 1.07 19NOV14 | Fixed error on internal gains & unprotect design condition cells
Version N5ae 1.08 22JAN15 | Fixed loced cells error in skylights
Version N5ae 1.09 19AUG16 | Fixed Blower Load Bug

## Comments
Enter any comments related to this job here.
Copy digital photos or create hyperlinks to additional information here.

## Wrk E (hidden)
Worksheet E -- Internal Loads
|  |  |  | Type of space load: | Zone | Month | Jul & Aug | Hour | 15:00
Part 1 -- Sensible Load for Lighting Fixtures (Btuh)
Table 6A Description and Table 6-10 Code |  |  | Troffer in | Fixture | Number | Diversity | Fixture | SF | Space | CLTD Adjustment |  | Space | Return | LFG for
|  |  | DAC Ceiling | Watts | Fixtures | Factor | Gain | Table | Gain | TM Code | CLF | Load | Air Load | DAC HB
|  |  | Yes = 1 | (FW) | (N) | DF = 1.0 | (LFG) | 6A-10 | (SLG) |  | DF = 1.0 | (SLL) | (RLL) | Calc
a |  |  |  | 1005 | 1 | 1 | 3430.065 | 1 | 3430.065 | d | 1 | 3430.065 | 0 | 0
b |  |  |  | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 0 | 0 | 0
c |  |  |  | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 0 | 0 | 0
d |  |  |  | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 0 | 0 | 0
SLL total goes to Form N1, Line 12a. RLL total goes to Worksheets D1, D2, RAP-1 and RAP-2 | [10 empty] | Totals = | 3430.065 | 0 | 0
1) Description: Table number with (as applicable) length, lamp type code, ballast type, number lamps, etc. Table 6A-10 code (S, RT, RTDD, RTSD) 2) LFG = 3.413 x FW x N x DF SLG = LFG x SF SLL for Form N1 = SLG x CLF RLL for Table 4B Construction 17C or 17D = LGF x RAF = LGF x (1 - SF)
Part 2 -- Sensible and Latent Load for Occupants (Btuh) | [15 empty] | For Wrk H
Occupant Activities Table 6B |  |  |  |  | Count | Sensible | Latent | Diversity | Sensible | CLTD Adjustment |  | Sensible | Latent |  |  | Effective # | Total
[5 empty] | (N) | Value | Value | Factor | Gain | TM Code | CLF | Load | Load |  |  | Occupants | Gain
[6 empty] | (Btuh) | (Btuh) | DF = 1.0 | (SG) |  | DF = 1.0 | (SCL) | (LCL) |  |  | N x DF | (SG)
a | Seated, eating a meal |  |  |  | 58 | 275 | 275 | 0.9 | 14355 |  | 1 | 14355 | 14355 |  |  | 52 | 28710
b | Seated, bar or conference room |  |  |  | 12 | 245 | 155 | 0.9 | 2646 |  | 1 | 2646 | 1674 |  |  | 11 | 4320
c | Standing, light work |  |  |  | 4 | 250 | 200 | 0 | 0 |  | 1 | 0 | 0 |  |  | 0 | 0
d | 0 |  |  |  | 0 |  |  | 0 | 0 |  | 1 | 0 | 0 |  |  | 0 | 0
[6 empty] | Total occupant loads for Form N1, Line 12b = | [5 empty] | 17001 | 16029 |  | Total = | 63
SG = N x DF x Sensible Value SCL = SG x CLF LCL = N x DF x Latent Value
Part 3 -- Sensible and Latent Load for Office Equipment Loads (Btuh)
Item Table 6C |  |  | Either Watts or Btuh |  | Count | Sensible | Latent | Diversity | Sensible | CLTD Adjustment |  | Sensible | Latent |  | Duty Cylce Calculator
|  |  | Item | Item | (N) | Value | Value | Factor | Gain | TM Code | CLF | Load | Load |  | DCF = Sum(LFi x UFi) Calculator
|  |  | Watts | Btuh |  | (Btuh) | (Btuh) | DF = 1.0 | (SG) |  | DF = 1.0 | (SCL) | (LCL) |  | Portion | LF | Portion | UF
a |  |  | 0 | 200 | 2 | 200 | 0 | 0.5 | 200 |  | 1 | 200 | 0 |  | 1 |  | 1
b |  |  | 119.455 | 0 | 1 | 119.455 | 0 | 0.5 | 59.7275 |  | 1 | 59.7275 | 0 |  | 2 |  | 2
c |  |  | 68.26 | 0 | 1 | 68.26 | 0 | 0.5 | 34.13 |  | 1 | 34.13 | 0 |  | 3 |  | 3
d |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 0 | 0 |  | 4 |  | 4
|  |  | Total office equipment loads for Form N1, Line 12c = | [8 empty] | 293.8575 | 0 |  | 5 |  | 5
Sensible Value = 3.413 x Item Watts or Item Btuh value from Table 6C SG = N x DF x Sensible Value SCL = SG x CLF LCL = N x DF x Latent Value | [14 empty] | DCF = | 0 | Sum = | 0
Part 4 -- Sensible Load for Motors and Motor-Driven Equipment (Btuh) | [14 empty] | Copy DCF to Column T
Item Table 6D |  | Efficiency | Config | Load | Use | Duty | Duty | Stored or | Duty | Number | CLTD Adjustment |  | Sensible
|  | (FLME) | Min-Ein = 1 | Factor | Factor | Cycle | Cycle | Exported | Cycle | (N) | TM Code | CLF | Load |  | DCF from Calculator |  |  | DCF form
| Power | Must be > 0 | Mout-Ein = 2 | (LF) | (UF) | Factor | Power | Energy | Gain |  |  | DF = 1.0 | (SCL) |  | Config | Config | Config | Cell
| (RHP) | DF = 1.00 | Min-Eout = 3 | Or blank & use DCF Calculator |  | (DCF) | (DCP) | (Btuh) | (DCG) | [5 empty] | 1 | 2 | 3 | R37
a |  | 1 |  |  |  | 0 | 0 |  | 0 |  |  | 1 | 0 |  | 0 | 0 | 0
b |  | 1 |  |  |  | 0 | 0 |  | 0 |  |  | 1 | 0 |  | 0 | 0 | 0
c |  | 1 |  |  |  | 0 | 0 |  | 0 |  |  | 1 | 0 |  | 0 | 0 | 0
d |  | 1 |  |  |  | 0 | 0 |  | 0 |  |  | 1 | 0 |  | 0 | 0 | 0
[7 empty] | Total motor load for Form N1, Line 12e = | [5 empty] | 0
DCF = Sum(LFi x UFi) DCP = RHP x DCF For motor and equipment in: DCG = (2,545 x DCP) / FLME - Stored Energy For motor out, equipment in: DCG = 2,545 x DCP - Stored Energy For motor in, equipment out: DCG = (2,545 x DCP) / FLME - 2,545 x DCP See Section 8 for energy calculations SCL = DCG x N x CLF
Part 5 -- Sensible and Latent Load for Food Service Equipment (Btuh)
Equipment Item Table 6E |  |  |  | Hooded | Exhaust | Make-Up | Sensible | Latent | Number | CLTD Adjustment |  | Sensible | Latent
|  |  |  | Yes = 1 | Cfm | Cfm | Value | Value | (N) | TM Code | CLF | Load | Load
|  |  |  | No = Blank |  |  | (Btuh) | (Btuh) |  |  | DF = 1.0 | (SCL) | (LCL)
a | [10 empty] | 1 | 0 | 0
b | [10 empty] | 1 | 0 | 0
c | [10 empty] | 1 | 0 | 0
d | [10 empty] | 1 | 0 | 0
[11 empty] | Totals = | 0 | 0
SCL = Sensible Value x N x CLF SCL = Latent Value x N
Part 6 -- Sensible Load for Hot Pipes (Btuh)
Hot Pipe Item Table 6G-1; 6G-2 |  |  |  |  | Length | Diameter | Wall TD | Insul. | Pipe | Sensible | CLTD Adjustment |  | Sensible
[5 empty] | (Ft) | (Inches) | (°F) | R-Value | Factor | Gain | TM Code | CLF | Load
[8 empty] | Bare = Blank | 6G-1; 6G-2 | (SG) |  | DF = 1.0 | (SCL)
a | [9 empty] | 0 |  | 1 | 0
b | [9 empty] | 0 |  | 1 | 0
c | [9 empty] | 0 |  | 1 | 0
d | [9 empty] | 0 |  | 1 | 0
| Total hot pipe load for Form N1, Line 12e = | [11 empty] | 0
For bare pipe: SG = 1.1 x Length x Factor For Insulated Pipe: SG = 1.1 x Length x TD x Factor SCL = SG x CLF
Part 7 -- Sensible Load for Hot Surfaces (Btuh)
Hot Surface Item Table 6G-3 |  |  |  | Surface | Surface | Surface | Wall TD | Surface | Surface | Sensible | CLTD Adjustment |  | Sensible
|  |  |  | Position | Material | Color | (°F) | Area | Factor | Regain | TM Code | CLF | Load
[8 empty] | (SqFt) | 6G-3 | (SRG) |  | DF = 1.0 | (SCL)
a | [9 empty] | 0 |  | 1 | 0
b | [9 empty] | 0 |  | 1 | 0
c | [9 empty] | 0 |  | 1 | 0
d | [9 empty] | 0 |  | 1 | 0
| Total hot surface load for Form N1, Line 12e = | [11 empty] | 0
SG = Area x Factor SCL = SG x CLF
Part 8 -- Cold Pipe Cooling Effect (Btuh)
Cold Pipe Item Table 6H-1 |  |  |  |  | Length | Diameter | Wall TD | Insul. | Pipe | Sensible | CLTD Adjustment |  | Sensible
[5 empty] | (Ft) | (Inches) | (°F) | R-Value | Factor | Gain | TM Code | CLF | Load
[9 empty] | 6H-1 | (SG) |  | No Effect | (SCL)
a | [9 empty] | 0 | ~ | 1 | 0
b | [9 empty] | 0 | ~ | 1 | 0
c | [9 empty] | 0 | ~ | 1 | 0
d | [9 empty] | 0 | ~ | 1 | 0
| Total cold pipe load for Form N1, Line 12f (negative load) = | [11 empty] | 0
For Insulated Pipe: SG = 1.1 x Length x TD x Factor SCL = SG x CLF
Part 9 -- Cold Storage Case Cooling Effect (Btuh)
Type of Storage Case Table 6H-2 | [5 empty] | Case | Sensible | Latent | Sensible | CLTD Adjustment |  | Sensible | Latent
[6 empty] | Length | Factor | Factor | Regain | TM Code | CLF | Load | Load
[6 empty] | (Ft) | 6H-2 | 6H-2 | (SRG) |  | No Effect | (SCL) | (LCL)
a | [8 empty] | 0 | ~ | 1 | 0 | 0
b | [8 empty] | 0 | ~ | 1 | 0 | 0
c | [8 empty] | 0 | ~ | 1 | 0 | 0
d | [8 empty] | 0 | ~ | 1 | 0 | 0
| Total cold case load for Form N1, Line 12f (negative load) = | [10 empty] | 0 | 0
SRG = Length x Sensible Factor SCL = -SRG (negative space load) LCL = Length x Latent Factor
Part 10 -- Sensible and Latent Load for Steam Release and Latent Load Evaporation from Wet Surface (Btuh)
Moisture Gain Item Table 6I-1; 6I-2 |  |  |  | Steam | Steam to | Wet | Wet Surface | Sensible | Latent | CLTD Adjustment |  | Sensible | Latent
|  |  |  | Release | Space TD | Surface | Temp | Factor | Factor | TM Code | CLF | Load | Load
|  |  |  | (Lb / Hr) | (°F) | Area (SqFt) | (°F) | 6I-1 or | 6I-1 or |  | No Effect | (SCL) | (LCL)
[8 empty] | 6I-2 | 6I-2
a | Steam 1 | [8 empty] | ~ | 1 | 0 | 0
b | Steam 2 | [8 empty] | ~ | 1 | 0 | 0
c | Wet Surface 1 | [8 empty] | ~ | 1 |  | 0
d | Wet Surface 2 | [8 empty] | ~ | 1 |  | 0
Total steam and wet surface load for Form N1, Line 12e = | [11 empty] | 0 | 0
For steam: SCL = 0.45 x Lb/Hr x Steam to Space TD and LCL = 1,050 x Lbs / Hr For wet surface: LCL = Latent Factor x Surface Area
Part 11 - Latent Load for Indoor Plants
Inventory of Indoor Plants | [9 empty] | Size | Latent | Number | Latent
[11 empty] | Btuh per | (N) | Load
[11 empty] | Plant |  | (LCL)
a | [9 empty] | Small | 10 | 0 | 0
b | [9 empty] | Medium | 20 | 0 | 0
c | [9 empty] | Large | 30 | 0 | 0
| Total indoor plant load for Form N1, Line 12b = | [11 empty] | 0
LCL = Btuh per Plant x N
Part 12 - Hygroscopic Load or Regain for a Steady State Flow Hygroscopic Materials (Btuh)
Hygroscopic Item Table 6J | [5 empty] | Pounds | RH of | Moisture | RH of | Moisture | Product | Sensible | Latent
[6 empty] | of Material | Entering | Content | Leaving | Factor | Hydration | Load | Load
[6 empty] | per Hour | Material | Entering | Material | Leaving | Rate (PHR) | (SCL) | (LCL)
[8 empty] | (MCin) |  | (MCout) | Lbs/Hr
a | [10 empty] | 0 | 0 | 0
b | [10 empty] | 0 | 0 | 0
c | [10 empty] | 0 | 0 | 0
d | [10 empty] | 0 | 0 | 0
| Total positive or negative load for Form N1, Line 12e = | [10 empty] | 0 | 0
Pounds material per Hour = Pounds of hygroscopic material flowing through the space per hour (or equivalent flow rate for non-continuous flow). PHR = Pounds per Hour x (MCin - MCout) Note: PRH may be positive (dehydration, moisture released to pace air) or negative (hydration, moisture absorbed from space air) LCL = ± 1,050 x PHR SCL = - Latent Load (CLF for sensible gain = 1.0)
Part 13 -- Internal Loads that Require Investigation
Electric or Fuel Equipment |  |  | Either Watts or Btuh |  | Count | Sensible | Latent | Diversity | Sensible | CLTD Adjustment |  | Sensible | Latent
Tables 6F-1, 6F-2 and 6F-3 |  |  | Item | Item | (N) | Value | Value | Factor | Gain | TM Code | CLF | Load | Load
|  |  | Watts | Btuh |  | (Btuh) | (Btuh) | DF = 1.0 | (SG) |  | DF = 1.0 | (SCL) | (LCL)
a | [5 empty] | 0 |  | 1 | 0 |  |  | 0 | 0
b | [5 empty] | 0 |  | 1 | 0 |  |  | 0 | 0
c | [5 empty] | 0 |  | 1 | 0 |  |  | 0 | 0
Total equipment load for Form N1, Line 12e = | [11 empty] | 0 | 0
Sensible Value = 3.413 x Item Watts or Item Btuh value SG = N x DF x Sensible Value SCL = SG x CLF LCL = N x DF x Latent Value
Summary for Form N1 | [8 empty] | Return
[6 empty] | Sensible | Latent |  | Air Load
a | Lighting Fixtures |  |  |  |  | 3430.065 | ~ |  | (RLL)
b | Occupants and Plants |  |  |  |  | 17001 | 16029 |  | 0
c | Office Equipment |  |  |  |  | 293.8575 | 0
d | Food Service Equipment and Investigated Loads |  |  |  |  | 0 | 0
e | DT-fan, Motor, Pipe, Hot/Wet Surface, Steam, Hygros |  |  |  |  | 0 | 0 | < Draw through fan is on Wks I and this fan load is added to line e loads on Form N1
f | Regain for Cold Storage or Pipe (negative cooling load) |  |  |  |  | 0 | 0

## Wrk F (hidden)
Worksheet F -- Infiltration Loads
|  |  | Type of space load: | Zone | Month | Jul & Aug | Hour | 15:00
Month | Hour | HTD | CTD | D Grains | Elevation | ACF | Type of Space (room #, zone # or block)
Jul & Aug | 0.625 | 26 | 13 | 3 | 39 | 1 | Zone
Part 1-- Determine Space Infiltration Cfm for Neutral Space Pressure
Option 1 — ACH Defaults (Tables 5A, 5B, 5C and 5D) |  |  |  |  | Apply = 1 > | 1 | Table Used for this Calculation > |  |  | 5C
Operating | Floor | Leakage | Space ACH | AGV | Space | Fireplace | Total ICFM | Total ICFM = Space CFM + FP CFM Space ICFM = ACH x AGV / 60 AGV = Above grade volume of heated or air conditioned space.
Mode | Area | Class | (Note 1) | (CuFt) | CFM | CFM | (Note 2)
(SqFt)
Heating | 1117 | Average | 0.62 | 13404 | 138.508 |  | 138.508
Cooling | 1117 |  | 0.33 | 13404 | 73.722 |  | 73.722
1) Res construction: Table 5A, 5B; Com. construction: Table 5C, 5D 2) The blower door method may be used to estimate ICFM values.
Option 2 — Blower Door Method |  |  |  |  | Apply = 2 > | [7 empty] | TR |  |  | HTG CFM |  |  | CLG CFM |  | RPM |  | CFM | HTG CFM | CLG CFM | [9 empty] | HTG CFM | CLG CFM
Operating | HTD | Wind | Blower | Table 5E |  |  | ICFM | Default heating season velocity = 15.0 MPH Default cooling season velocity = 7.5 MPH ELA4 value p provided by field test. |  |  |  |  | 5 | 2 | 5 | 149 | 9 | 12 | 74 |  | 0 | 0 | 0
Mode | and | Velocity | Door | Cs | Shielding | Cw | [6 empty] | 10 | 3 | #N/A |  | 10 | #N/A |  |  | 1 | 200
| CTD | (MPH)Total | ELA4 |  | Class | [7 empty] | 15 | 4 | #N/A |  | 11 | #N/A |  |  | 2 | 400
Heating |  | 15 |  |  |  |  | 0 | ICFM = ELA4 x ( Cs x TD + Cw x V2 ) 0.50 |  |  |  |  | 25 | 5 | #N/A |  | 12 | #N/A |  |  | 3 | 400
Cooling |  | 7.5 |  |  |  |  | 0 | [5 empty] | 50 | 6 | #N/A |  | 13 | #N/A |  |  | 4 | 400
[13 empty] | 100 | 7 |  | 149 | 14 |  | 74 |  |  |  | 0 | 149 | 74 | [9 empty] | 149 | 74
Part 2 -- Determine Door Infiltration Cfm | [12 empty] | 200 | 8 |  |  | 15
Normal Use Door (Table 5F) |  |  |  | Overhead Door (Table 5G)
Item ID | TR | Heat Cfm | Cool Cfm | Item ID | Cycle/Dr/Hr | H-Cfm/ SF | C-Cfm/SF | Area (SF) | Heat Cfm | Cool Cfm | Code ID | Heating | 5 | 10 | 15 | 25 | 50 | 100 | 200 | 5 | 10 | 15 | 25 | 50 | 100 | 200
|  | 149 | 74 | [7 empty] | 5F-ssd | 5F-ssd-nv Single Swinging Door (21 SqFt), no vestibule | 30 | 59 | 89 | 149 | 297 | 594 | 1189 | 15 | 29 | 44 | 74 | 147 | 295 | 590
[11 empty] | 5F-ssd | 5F-ssd-v Single Swinging Door (21 SqFt), with vestibule | 30 | 59 | 89 | 149 | 297 | 594 | 637 | 15 | 29 | 44 | 74 | 147 | 295 | 316
[11 empty] | 5F-dsf | 5F-dsf-nv Double Swinging Door (42 SqFt), no vestibule | 59 | 119 | 178 | 297 | 594 | 1189 | 2377 | 29 | 59 | 88 | 147 | 295 | 590 | 1179
[11 empty] | 5F-dsd | 5F-dsd-v Double Swinging Door (42 SqFt), with vestibule | 59 | 119 | 178 | 297 | 594 | 1189 | 1274 | 29 | 59 | 88 | 147 | 295 | 590 | 632
[11 empty] | 5F-sad | 5F-sad-nv Single Automatic Door (21 SqFt), no vestibule | 80 | 161 | 241 | 402 | 803 | 1607 | 3213 | 40 | 80 | 119 | 199 | 398 | 796 | 1592
Totals = |  | 149 | 74 |  |  |  | Totals = |  | 0 | 0 | 5F-sad | 5F-sad-v Single Automatic Door (21 SqFt), with vestibule | 54 | 107 | 161 | 268 | 356 | 1071 | 2142 | 27 | 53 | 80 | 133 | 266 | 631 | 1063
[11 empty] | 5F-dad | 5F-dad-nv Double Automatic Door (42 SqFt), no vestibule | 161 | 321 | 482 | 803 | 1607 | 3213 | 6426 | 80 | 159 | 239 | 398 | 796 | 1592 | 3184
Part 3 -- Total Infiltration Cfm to Conditioned Space for Neutral Space Pressure | [10 empty] | 5F-dad | 5F-dad-v Double Automatic Door (42 SqFt), with vestibule | 107 | 214 | 321 | 536 | 1071 | 2142 | 4284 | 53 | 106 | 159 | 266 | 531 | 1063 | 2125
ICFM equals the sum of space Cfm, NU door Cfm and OH door Cfm |  | Total Cfm for Heating |  |  |  |  | Total Cfm for Cooling |  |  |  | 5F-mrd | 5F-mrd Manual revolving Door | 4 | 9 | 13 | 21 | 43 | 85 | 170 | 4 | 9 | 13 | 21 | 43 | 85 | 170
|  | Space | NU Door | OH Door | ICFM |  | Space | NU Door | OH Door | ICFM | 5F-ard | 5F-ard Automatic Revolving Door
|  | 138.508 | 149 | 0 | 287.508 |  | 73.722 | 74 | 0 | 147.722 | [16 empty] | TR |  | Column |  | Column | H-CFM/Sq. Ft. | C-CFM/Sq. Ft. | Sq. Ft. | HTG CFM | CLG CFM
[13 empty] | 1 | 2 | 3 | 4 | 6 | 8 | 10 | 1 | 2 | 3 | 4 | 6 | 8 | 10 | 1 | 2 |  | 9 |  | #N/A | #N/A | 0
Part 4 — Infiltration Loads on Central Equipment Adjusted for space pressure | [11 empty] | OH-1 Engineered relief area equal to or greater than door area, or equivalent mechanical exhaust, or extremely loose construction. R=1.0 | 8.3 | 16.5 | 24.8 | 33 | 49.5 | 66 | 82.5 | 4.1 | 8.2 | 12.4 | 16.5 | 24.8 | 33 | 41.3 | 2 | 3 |  | 10 |  | #N/A | #N/A | 0
[12 empty] | OH-2 Considerable engineered relief, envelope leakage area about 80% of the door area. R=0.80 | 6.6 | 13.2 | 19.8 | 26.4 | 39.6 | 52.8 | 66 | 3.3 | 6.6 | 9.9 | 13.2 | 19.8 | 26.4 | 33 | 3 | 4 |  | 11 |  | #N/A | #N/A | 0
| 38219.6161 | < Sensibel load for default AH Cfm | [9 empty] | OH-3 Sinificant engineered relief, envelope leakage area about 65% of the door area. R=0.65 | 5.4 | 10.7 | 16.1 | 21.5 | 32.2 | 42.9 | 53.6 | 2.7 | 5.4 | 8 | 10.7 | 16.1 | 21.5 | 26.8 | 4 | 5 |  | 12 |  | #N/A | #N/A | 0
Type of | AH Supply | Other | Exhaust | AH Return | Case # | CFMimb | ICFM | NCFM | Effective | H & C |  | OH-4 Some engineered relief, envelope leakage area about 50% of the door area. R=0.50 | 4.1 | 8.3 | 12.4 | 16.5 | 24.8 | 33 | 41.3 | 2.1 | 4.1 | 6.2 | 8.3 | 12.4 | 16.5 | 20.6 | 6 | 6 |  | 13 |  | #N/A | #N/A | 0
Load | Cfm | Supply | Cfm | Cfm | Table 5H | Table 5H | Part 3 | Table 5H | ACH | Loads |  | OH-5 No engineered relief, envelope leakage area much smaller than door area. R=0.35 | 2.9 | 5.8 | 8.7 | 11.6 | 17.3 | 23.1 | 28.9 | 1.4 | 2.9 | 4.3 | 5.8 | 8.7 | 11.6 | 14.4 | 8 | 7 |  | 14 |  |  |  |  | 0 | 0
|  | Cfm | [6 empty] | (NACH) | (Btuh) | [16 empty] | 10 | 8 |  | 15
Heat Load |  |  |  |  | 2 | 0 | 287.508 | 287.508 | 1.287 | 8222.7288
Sens Load |  |  |  |  | 2 | 0 | 147.722 | 147.722 | 0.66124 | 2112.4246
Lat Load |  |  |  |  | 2 |  |  | 287.508 |  | 301.3529
Default AH Supply Cfm = (Sum of sensible cooling loads on Form N1, Lines 6 through 12) / (1.1 x 20 x ACF) CFMimb equals the excess Cfm delivered to the space, or the excess Cfm extracted from the space. Heating Load = 1.1 x ACF x NCFM x HTD; Sensible Load = 1.1 x ACF x NCFM x CTD ; Latent Load = 0.68 x ACF x NCFM x D Grains Supply air, return air and exhaust systems shall be balanced for desired space pressure condition and CFMimb value.
1) The room or space infiltration load equals the block infiltration load multiplied by the gross wall area ratio (WAR). 2) WAR = Gross room or space wall area / Gross wall area for all rooms and spaces served by central equipment.
Table 5H
Case 1 – Space Pressurized |  |  | CFMimb = (Air handler Supply Cfm + Other Supply Cfm) - (Air handler Return Cfm + Exhaust Cfm)
CFMimb > 0.30 x ICFM |  |  | NCFM = (ICFM^2- CFMimb^2 )^ 0.5 |  |  | Heat = | 287.508 | Cool = | 147.722
Case 2 – Neutral Pressure |  |  | NCFM = ICFM = CFMinf
CFMimb ≤ 0.30 x ICFM |  |  | No pressure adjustment required. |  |  | Heat = | 287.508 | Cool = | 147.722
Case 3 – Negative pressure |  |  | CFMimb = (Air handler Return Cfm + Exhaust Cfm) - (Air handler Supply Cfm + Other Supply Cfm)
CFMimb > 0.30 x ICFM |  |  | NCFM = (ICFM^2+ CFMimb^2 ) ^0.5 |  |  | Heat = | 287.508 | Cool = | 147.722

## D2 (hidden)
Evaluate lighting loads on Worksheet E before using this worksheet!
Worksheet D2
Ceiling Load for a Return Air Plenum Under a Conditioned Space
|  |  | Type of space load: | Zone | Month | Jul & Aug | Hour | 0.625
Design Conditions and Surface Areas and Plenum Temperature for Cooling
Month | Hour | Indoor DB | ACF | Floor Area | Ceiling | [5 empty] | Adj PT for
|  | IAT | T10A | Under Floor | Area | [5 empty] | Cooling | Heat balance heating = 0.0 ± 1.0
#REF! | #REF! | #REF! | #REF! |  | 0 | [5 empty] | 80 | #REF! | <- if negative, decrease PT; if positive, increase PT
IAT = Indoor design dry bulb for midsummer (default = 75 ºF) | [11 empty] | 100x
PT is the heat balance temperature for the plenum (trial and error value).
[13 empty] | < Aprox PT for Wrk D3, when used | For Wrk D3, when used
Floor HTM for Cooling
Table 4A; Item 17D |  | Floor | Floor | Floor | [7 empty] | -75 | < PTDC for Worksheet D if D3 not used
Construction No. |  | U-Value | HTM - | PTDC
|  |  | for HB | (CLTD) | [7 empty] | 75 | < Space db
|  |  | #REF! | -75
Floor HTM = - Floor U-Value x (PT - IDB); Floor PTDC = PT - IDB
Lighting HTM for Cooling |  |  |  | Ceiling HTM for Cooling |  |  |  | Return Air HTM for Cooling
RLL | Other | Gross | Lighting | Ceiling | Ceiling | Ceiling | Ceiling | Form N1 | Floor | Default | RA
Btuh | Plen Loads | Ceiling | HTM + | Material | U-value | HTM (-) | PTDC | Lines 6-13 | Area | ALF for | HTM (-)
Wks E | Btuh | Area | for HB |  | T4A-17D | for HB | (CLTD) | Btuh | SqFt | Cooling | for HB
0 |  | 0 | #DIV/0! |  |  | #REF! | -75 | 40332.0407 | 0 | #REF! | #REF!
RLL = Lighting load to return air from WKs E; Other Loads = Other electric-mechanical gains to RA plenum | [9 empty] | known
Lighting HTM = (RLL + Other Loads) / Gross Ceiling Area | [9 empty] | value
Ceiling HTM = - Ceiling U-Value x (PT - IAT); Ceiling PTDC = PT - IAT
For estimating ceiling load: Default ALF = Form N1 sensible sum for lines 6 through 13 / (1.1 x ACF x 20 x Floor Area); or known value
Use Worksheet RAP-1 to calcuate return air load and duct load.
RA HTM = - 1.1 x ACF x ALF x (PT - IAT)
Plenum Heat Balance for Cooling |  |  |  |  | Ceiling and Floor Loads for This Scenerio
Floor | Lighting | Ceiling | RA | Sum of | Ceiling | Ceiling | Ceiling | Floor | Floor | Floor | Heating
HTM (-) | HTM (+) | HTM (-) | HTM (-) | HTMs | Area | HTM for | Load for | Area | HTM for | Load for | Loads
[5 empty] | SqFt | Cooling | Cooling | SqFt | Cooling | Cooling
#REF! | #DIV/0! | #REF! | #REF! | #REF! | 0 | #REF! | #REF! | 0 | #REF! | #REF! | Zero
The estimated value for plenum temperature (PT) is correct if sum of HTMs = zero (range = ± 1.0)
The ceiling and floor HTMs for cooling are absolute values (use a positive values).
Ceiling load for cooling (Btuh) = Ceiling HTM for cooling x Ceiling area
Floor load for cooling (Btuh) = Floor HTM for cooling x Floor area
The ceiling and floor loads are space loads for two different spaces (see assignment note below).
To simplify the procedure for heating, there is no adjustment for lighting, floor and ceiling effects.
Return Air Loads and Duct Loads for a Return Air Plenum Below a Conditioned Space
Worksheet RAP-2 is used to evaluate the load to the return air flowing through the plenum and the load for duct runs in a return air plenum. Also see Table 7-AMB and Worksheet G.
Assignment of Ceiling and Return Air Loads
For cooling, there is a ceiling load for the room or space below the return air plenum and a floor load for the room or space above the return air plenum. The return air load for cooling is a system load (part of the total load on the central equipment).
The ceiling HTM for cooling appears on Worksheet D, Construction 17C.
The ceiling HTM, load area and cooling load appear on Form N1, Line 10.
The floor HTM for cooling appears on Worksheet D, Construction 17D.
The floor HTM, load area and cooling load appear on Form N1, Line 11.
The ceiling and floor loads appear on the same forms if both spaces contribute to a block load or zone load.
Return air loads appear on Worksheet RAP-2, Worksheet G and on Form N1, Line 15.
Note on L21: ALF for load in cell J27

## D3 (hidden)
Worksheet D3
Ceiling and Floor Load for Return Air Plenum Under a Roof and Under a Conditioned Space
|  |  | Type of space load: | Zone | Month | Jul & Aug | Hour | 15:00
Procedure:
1) Determine the floor area for the space under the return air plenum (part of this area will be under a roof and part will be under a conditioned space).
2) Perform D1 heat balance calculations for heating and cooling using the entire floor area of the space covered by the return air plenum.
3) Perform D2 heat balance calculations for heating and cooling using the entire floor area of the space covered by the return air plenum.
4) Determine the floor area for the portion of the space that is under the roof. | [8 empty] | Total floor area = | 0
5) Determine the floor area for the portion of the space that is under a conditioned space. | [8 empty] | Floor area under roof = | 0
6) Use the following form to calculate the weighted average plenum temperature for cooling and heating. | [8 empty] | Floor area under floor = | 0
7) Use the following form to calculate the weighted average return air loads for cooling and heating.
Average Ambient Temperature for Worksheet G
Weighted average plenum temp for cooling | [6 empty] | Weighted average plenum temp for heating
Output | Amb DB | Actual | Total | Average |  |  | No ceiling or floor load for heating on Uorksheet D or lines 11 and 12 of Form N1. Use Worksheet RAP-3 to evaluate the return air load for heating (line 15 of Form N1).
From | Cooling | SqFT | SqFT | Plenum
| PT value |  |  | Temp °F
D1 | #REF! | 0 | 0 | #REF!
D2 | 0 | 0
Actual SqFt = floor area under roof for D1 and floor area under conditioned space for D2
Weighted average temperature = (D1 Pt x Floor area under roof + D2 Pt x Floor area under c-space) / Total floor area
Ceiling HTM = Ceiling U-Value x Ceiling PTDC Where: Ceiling PTDC = PT - IAT
Use Worksheet RAP-3 to calculate return air loads and duct loads for heating and cooling.
Avg PT | Space db
#REF! | 75 | #REF! | < PTDC for Worksheet D

## DAC-1 (hidden)
Worksheet DAC-1
Dead Air Cavity Under a Roof
|  |  | Type of space load: | Zone | Month | Jul & Aug | Hour | 15:00
Design Conditions and Surface Areas and Plenum Temperature for Cooling
Month | Hour | Latitude | Summer DB | Indoor DB | Day Range | ACF | Floor Area | Roof | Gross | Gross | Adj CT for
|  |  | OAT | IAT (mo) | °F | T10A | Under Roof | Slope Deg | Roof Area | Ceil Area | Cooling | Heat balance heating = 0.0 ± 1.0
Jul & Aug | 0.625 | 34 | 88 | 75 | 20 | 1 |  |  | 0 |  |  | #DIV/0! | <- if negative, decrease PT; if positive, increase PT
OAT = Midsummer design temperature for city (Table 1 or alternative value); IAT = Indoor design dry bulb for midsummer (default = 75 ºF) | [11 empty] | 100x
CT is the heat balance temperature for the dead air cavity (trial and error value).
[12 empty] | 83 | < Aprox CT
Roof HTM for Cooling | [11 empty] | 1.5 | < ∆ Grains
Table 4A; Item 17C |  | Roof | Group | Base CLTD | Roof | Mo-Lat | Color | DR | Adjusted |  | Roof
Construction No. |  | U-Value | Number | T4B-17A | Color | Adj | Factor | Adjust | CLTD |  | HTM + | For Wrk G (DAC-3 not used)
[6 empty] | No = Blank | No = Blank | No = Blank |  |  |  | For Wrk DAC-3 when used
[9 empty] | 68 |  | 0
Base CLTD provided by Table 14B, Construction 17A; Mo-Lat, color and daily range adjustments from same page.
Adjusted CLTD = (Base CLTD + Lat/Mo Correction) x Color Factor + (OAT - 95) + (75 - CT) + DR Adjustment
Roof HTM = Roof U-value x Adjusted CLTD
Lighting HTM for Cooling | [5 empty] | Ceiling HTM for Cooling
Total | DAF | Lighting | Other | Gross | Lighting | Ceiling | Ceiling | Ceiling
LFG | from | Btuh to | Loads | Ceiling | HTM + | Material | U-value | HTM (-)
(Btuh) | Tbl 6A-10 | Cavity | Btuh | Area |  |  | T4A-17c
0 |  | 0 |  | 0 | #DIV/0! |  |  | 0
Total LFG = Total lighting fixture gain for troffers or cans in the ceiling (from Part 1, Worksheet E, as applicable).
Lighting Btuh to cavity = Total LFG x DAF from Table 6A-10; Other Loads = Other electric-mechanical gains to dead air cavity
Lighting HTM = (Lighting Btuh + Other Loads) / Gross Ceiling Area; Ceiling HTM = - Ceiling U-Value x (CT - IAT)
Heat Balance for Cooling |  |  |  |  | Grains |  |  |  |  | For Wrk G or DAC-3
Roof | Lighting | Ceiling | Sum of |  | Difference |  |  |  |  | Amb DB | DF Amb
HTM (+) | HTM (+) | HTM (-) | HTMs |  | from |  |  |  |  | Cooling | Grains
[5 empty] | Wrks A |  |  |  |  | CT value | Diff.
0 | #DIV/0! | 0 | #DIV/0! |  | 3 |  |  |  |  | 83 | 1.5
The estimated value for plenum temperature (CT) is correct if sum of HTMs = zero (range = ± 5.0).
Outdoor-indoor grains difference value is for month selected for the load calculation is provided by Worksheet A.
Tight cavity, leaky ceiling: Ambient Grains Difference = 0
Leaky cavity, tight ceiling: Ambient Grains Difference = Grains difference from Worksheet A
General default for ambient Grains = Worksheet A Grains / 2
Roof HTM for Heating |  |  | Ceiling HTM for Heating | [7 empty] | Adj CT for | Heat balance heating = 0.0 ± 1.0
Roof | Winter | Roof | Ceiling | Indoor | Ceiling | [5 empty] | Heating | 0 | <- if negative, decrease PT; if positive, increase PT
U-Value | Dry Bulb | HTM (-) | U-value | Dry Bulb | HTM (+) | [5 empty] | 59.66 | 100x
| OAT |  | T4A-17c | IAT
0 | 44 | 0 | 0 | 70 | 0
Heating calculations are made for the winter design temperature (OAT). No credit for heat gain from lighting or other electric-mechanical gains.
Roof HTM = - U-value x (CT - OAT) | [11 empty] | 59.66 | < Aprox CT
Ceiling HTM = Ceiling U-Value x (IAT - CT) ... Default IAT = 70 °F
For Wrk G (DAC-3 not used)
Heat Balance for Heating | [9 empty] | For Wrk G or DAC-3 |  | For Wrk RAP-3 when used
Roof | Ceiling | Sum of | [7 empty] | Amb DB
HTM (-) | HTM (+) | HTMs | [7 empty] | Heating
CT value
0 | 0 | 0 | [7 empty] | 59.66
The estimated value for plenum temperature (CT) is correct if sum of HTMs = zero (range = ± 1.0).

## DAC-2 (hidden)
Worksheet DAC-2
Dead Air Cavity Under a Conditioned Space
|  |  | Type of space load: | Zone | Month | Jul & Aug | Hour | 15:00
Design Conditions and Surface Areas and Plenum Temperature for Cooling
Month | Hour | Indoor DB | ACF | Day Range | Floor Area | Ceiling |  |  |  | Adj CT for
|  | IAT | T10A | °F | Under Floor | Area |  |  |  | Cooling | Heat balance heating = 0.0 ± 1.0
Jul & Aug | 0.625 | 75 | 1 | 20 |  | 0 |  |  |  | 80 | #DIV/0! | <- if negative, decrease PT; if positive, increase PT
OAT = Midsummer design temperature for city (Table 1 or alternative value); IAT = Indoor design dry bulb for midsummer (default = 75 ºF) | [10 empty] | 100x
CT is the heat balance temperature for the dead air cavity (trial and error value).
< Aprox CT
Floor HTM for Cooling | [10 empty] | Zero | < ∆ Grains
Table 4A; Item 17D |  | Floor | Floor
Construction No. |  | U-Value | HTM - | [7 empty] | For Wrk G (DAC-3 not used)
|  |  | 0 | [7 empty] | For Wrk DAC-3 when used
Floor HTM = - Floor U-Value x (CT - IDB)
Lighting HTM for Cooling | [5 empty] | Ceiling HTM for Cooling
Total | DAF | Lighting | Other | Gross | Lighting | Ceiling | Ceiling | Ceiling
LFG | from | Btuh to | Loads | Ceiling | HTM + | Material | U-value | HTM (-)
(Btuh) | Tbl 6A-10 | Cavity | Btuh | Area |  |  | T4A-17c
0 | 0.2 | 0 |  | 0 | #DIV/0! |  |  | 0
Total LFG = Total lighting fixture gain for troffers or cans in the ceiling (from Part 1, Worksheet E, as applicable).
Lighting Btuh to cavity = Total LFG x DAF from Table 6A-10; Other Loads = Other electric-mechanical gains to dead air cavity
Lighting HTM = (Lighting Btuh + Other Loads) / Gross Ceiling Area; Ceiling HTM = - Ceiling U-Value x (CT - IAT)
Heat Balance for Cooling | [6 empty] | For Wrk G or DAC-3 |  | For Worksheet G - Heating
Floor | Lighting | Ceiling | Sum of |  |  |  | Amb DB | DF Amb | Defult to duct runs in conditioned space. A duct load calcuation is not required for heating.
HTM (+) | HTM (+) | HTM (-) | HTMs |  |  |  | Cooling | Grains
[7 empty] | CT value | Diff.
0 | #DIV/0! | 0 | #DIV/0! |  |  |  | 0 | Zero
The estimated value for plenum temperature (CT) is correct if sum of HTMs = zero (range = ± 1.0).

## DAC-3 (hidden)
Worksheet DAC-3 | [12 empty] | SqFt of RA Ceiling Area
Dead Air Cavity Under a Roof and Under a Conditioned Space | [12 empty] | Space 1 | Space 2 | Space 3
|  |  | Type of space load: | Zone | Month | Jul & Aug | Hour | 15:00 |  |  |  | Space Name > |  |  |  | Totals
Procedure: | [11 empty] | SqFt under Roof > |  |  |  | 0
1) Determine the floor area for the space under the dead air cavity (part of this area will be under a roof and part will be under a conditioned space). | [11 empty] | SqFt under floor > |  |  |  | 0
2) Perform DAC-1 heat balance calculations for heating and cooling using the entire floor area of the space covered by the dead air cavity. | [14 empty] | Total = | 0
3) Perform DAC-2 heat balance calculations for heating and cooling using the entire floor area of the space covered by the dead air cavity.
4) Determine the floor area for the portion of the space that is under the roof. | [9 empty] | Total floor area =
5) Determine the floor area for the portion of the space that is under a conditioned space. | [9 empty] | Floor area under roof =
6) Use the following forms to calculate the weighted average cavity temperature for cooling and heating. | [9 empty] | Floor area under floor =
7) Use the following form to calculate the weighted average Grains for cooling.
Average Ambient Temperature for Worksheet G
Weighted average plenum temp for cooling (°F) | [6 empty] | Weighted average plenum temp for heating (°F)
Output | Amb DB | Actual | Total | Average |  |  | Output | Amb DB | Actual | Total | Average
From | Cooling | SqFT | SqFT | Cavity |  |  | From | Heating | SqFT | SqFT | Cavity
| CT value |  |  | Temp °F |  |  |  | CT value |  |  | Temp °F
DAC-1 | 83 | 0 | 0 | #DIV/0! |  |  | DAC-1 | 59.66 | 0 | 0 | #DIV/0!
DAC-2 | 59.66 | 0 |  |  |  |  | DAC-2 | 70 | 0
Actual SqFt = floor area under roof for DAC-1 and floor area under conditioned space for DAC-2
Weighted average temperature = (DAC-1 CT x Floor area under roof + DAC-2 CT x Floor area under c-space) / Total floor area
For DAC-2 heating the (CT - IAT) effect is ignored (the DAC-2 CT value equals indoor design temperature from Worksheet A).
Average Ambient Grains for Worksheet G
Weighted average Grains for latent cooling (Btuh)
Output | Ambient | Actual | Total | Average
From | ∆ Grains | SqFT | SqFT | ∆ Grains
DAC-1 | 1.5 | 0 | 0 | #DIV/0!
DAC-2 | 0 | 0
Actual SqFt = floor area under roof for DAC-1 and floor area under conditioned space for DAC-2
Weighted average Grains = (DAC-1 Grains x Floor area under roof + DAC-2 Grains x Floor area under c-space) / Total floor area
Cooling |  |  |  |  | Heating
#DIV/0! | < Avg CT for Wrk G |  |  |  | #DIV/0! | < Avg CT for Wrk G
#DIV/0! | < Avg ∆ Grains for Wrk G

## RAP-1 (hidden)
Worksheet RAP-1
Entire Return Air Plenum Under a Roof
|  |  | Type of space load: | Zone | Month | Jul & Aug | Hour | 15:00
Design Conditions and Surface Areas and Plenum Temperature for Cooling
Month | Hour | Latitude | Summer DB | Indoor DB | Day Range | ACF | Floor Area | Roof | Gross | Gross | Adj PT for
|  |  | OAT | IAT | °F | T10A | Under Roof | Slope Deg | Roof Area | Ceil Area | Cooling | Heat balance heating = 0.0 ± 1.0
Jul & Aug | 0.625 | 34 | 88 | 75 | 20 | 1 |  |  | 0 |  | 80 | #DIV/0! | <- if negative, decrease PT; if positive, increase PT
OAT = Midsummer design temperature for city (Table 1 or alternative value); IAT = Indoor design dry bulb for midsummer (default = 75 ºF) | [11 empty] | 100x
PT is the heat balance temperature for the plenum (trial and error value).
< Aprox PT
Roof HTM for Cooling | [12 empty] | < Sensible load to return air
Table 4A; Item 17C |  | Roof | Group | Base CLTD | Roof | Mo-Lat | Color | DR | Adjusted |  | Roof
Construction No. |  | U-Value | Number | T4B-17A | Color | Adj | Factor | Adjust | CLTD |  | HTM + | For Wrk G and G1 (RAP-3 not used)
[6 empty] | No = Blank | No = Blank | No = Blank |  |  |  | For Wrk RAP-3 when used
[9 empty] | -12 |  | 0
Base CLTD provided by Table 14B, Construction 17A; Mo-Lat, color and daily range adjustments from same page.
Adjusted CLTD = (Base CLTD + Lat/Mo Correction) x Color Factor + (OAT - 95) + (75 - PT) + DR Adjustment
Roof HTM = Roof U-value x Adjusted CLTD
Lighting HTM for Cooling |  |  |  | Ceiling HTM for Cooling |  |  | Return Air HTM for Cooling
RLL | Other | Gross | Lighting | Ceiling | Ceiling | Ceiling | Form N1 | SAT for | Floor | Default | RA
Btuh | Plen Loads | Ceiling | HTM + | Material | U-value | HTM (-) | Lines 6-13 | Cooling | Area | ALF for | HTM (-)
Wks E | Btuh | Area |  |  | T4A-17c |  | Btuh | °F | SqFt | Cooling
0 |  | 0 | #DIV/0! |  |  | 0 | #REF! | 55 | 0 | 0 | 0
RLL = Lighting load to return air from Wks E | [9 empty] | known
Other Loads = Other electric-mechanical gains to RA plenum | [9 empty] | value
Lighting HTM = (RLL + Other Loads) / Gross Ceiling Area
Ceiling HTM = - Ceiling U-Value x (PT - IAT)
Default ALF for cooling = Form N1, line 14 sensible load / (1.1 x ACF x (IAT - SAT) x Floor Area); or known value
Default SAT = 55 ºF; so default (IAT - SAT) = 20 º
RA HTM = - 1.1 x ACF x ALF x (PT - IAT)
Heat Balance for Cooling |  |  |  |  | Sensible |  |  |  | For Wrk G | For Wrk G1
Roof | Lighting | Ceiling | RA | Sum of | Load |  |  |  | Amb DB | Sensible | Latent
HTM (+) | HTM (+) | HTM (-) | HTM (-) | HTMs | to RA |  |  |  | Cooling | Load | Load
[9 empty] | PT value | to RA | to RA
0 | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  |  |  | 0 | 0 | Zero
The estimated value for plenum temperature (PT) is correct if sum of HTMs = zero (range = ± 5.0).
Sensible cooling load to RA (Btuh) = -RA HTM x FA … i.e, the cooling load is positive.
The return air load is a system load for Form N1, Line 15.
Roof HTM for Heating |  |  | Ceiling HTM for Heating |  |  | Return Air HTM for Heating |  |  |  |  | Adj PT for | Heat balance heating = 0.0 ± 1.0
Roof | Winter | Roof | Ceiling | Indoor | Ceiling | Form N1 | SAT for | Floor | Default | RA | Heating | 0 | <- if negative, decrease PT; if positive, increase PT
U-Value | Dry Bulb | HTM (-) | U-value | Dry Bulb | HTM (+) | Lines 6-13 | Heating | Area | ALF for | HTM (+) | 60 | 100x
| OAT |  | T4A-17c | IAT |  | Btuh | °F | SqFt | Heating
0 | 44 | 0 | 0 | 70 | 0 | #REF! | 100 | 0 | 0 | 0
Heating calculations are made for the winter design temperature (OAT). | [8 empty] | known
No credit for heat gain from lighting or other electric-mechanical gains. | [8 empty] | value
Roof HTM = - U-value x (PT - OAT) | [12 empty] | < Aprox PT
Ceiling HTM = Ceiling U-Value x (IAT - PT) ... Default IAT = 70 °F | [12 empty] | < Sensible load to return air
Default ALF for heating = Form N1, line 14 heating load / (1.1 x ACF x (SAT - IAT) x Floor Area); or known value
Default SAT = 100 ºF; so default (SAT - IAT) = 30 º
Note: If the blower operates the cooling Cfm year-around -- use the default ALF for cooling. | [8 empty] | <-- 1 = yes; 0 = no |  |  | For Wrk G and G1 (RAP-3 not used)
RA HTM = 1.1 x ACF x ALF x (IAT - PT) | [11 empty] | For Wrk RAP-3 when used
Heat Balance for Heating |  |  |  | Heating |  |  |  |  | For Wrk G | For Wrk G1
Roof | Ceiling | RA | Sum of | Load |  |  |  |  | Amb DB | Heating | Latent
HTM (-) | HTM (+) | HTM (+) | HTMs | to RA |  |  |  |  | Cooling | Load | Load
[9 empty] | PT value | to RA | to RA
0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | na
The estimated value for plenum temperature (PT) is correct if sum of HTMs = zero (range = ± 1.0).
Heating load to RA (Btuh) = -Roof HTM x Roof Area … i.e, the heating load is positive.
The return air load is a system load for Form N1, Line 15.
To simplify the procedure for heating, the roof load is assigned to the return air load with no adjustment for the ceiling effect.
Note on L22: ALF for load in cell I25

## RAP-2 (hidden)
Worksheet RAP-2
Entire Return Air Plenum Under a Conditioned Space
|  |  | Type of space load: | Zone | Month | Jul & Aug | Hour | 15:00
Design Conditions and Surface Areas and Plenum Temperature for Cooling
Month | Hour | Indoor DB | ACF | Floor Area | Ceiling | [5 empty] | Adj PT for
|  | IAT | T10A | Under Floor | Area | [5 empty] | Cooling | Heat balance heating = 0.0 ± 1.0
Jul & Aug | 0.625 | 75 | 1 |  | 0 | [5 empty] | 80 | #DIV/0! | <- if negative, decrease PT; if positive, increase PT
OAT = Midsummer design temperature for city (Table 1 or alternative value); IAT = Indoor design dry bulb for midsummer (default = 75 ºF) | [11 empty] | 100x
PT is the heat balance temperature for the plenum (trial and error value).
< Aprox PT
Floor HTM for Cooling | [12 empty] | < Sensible load to return air
Table 4A; Item 17D |  | Floor | Floor
Construction No. |  | U-Value | HTM - | [8 empty] | For Wrk G and G1 (RAP-3 not used)
|  |  | 0 | [8 empty] | For Wrk RAP-3 when used
Floor HTM = - Floor U-Value x (PT - IAT)
Lighting HTM for Cooling |  |  |  | Ceiling HTM for Cooling |  |  | Return Air HTM for Cooling
RLL | Other | Ceiling | Lighting | Ceiling | Ceiling | Ceiling | Form N1 | SAT for | Floor | Default | RA
Btuh | Plen Loads | Area | HTM + | Material | U-value | HTM (-) | Lines 6-13 | Cooling | Area | ALF for | HTM (-)
Wks E | Btuh |  |  |  | T4A-17c |  | Btuh | °F | SqFt | Cooling
0 |  | 0 | #DIV/0! |  |  | 0 | #REF! | 55 | 0 | 0 | 0
RLL = Lighting load to return air from WKs E; Other Loads = Other electric-mechanical gains to RA plenum | [9 empty] | known
Lighting HTM = (RLL + Other Loads) / Ceiling Area | [9 empty] | value
Other Loads = Other electric-mechanical gains to RA plenum
Ceiling HTM = - Ceiling U-Value x (PT - IAT)
Default ALF for cooling = Form N1, line 14 sensible load / (1.1 x ACF x (IAT - SAT) x Floor Area); or known value
Default SAT = 55 ºF; so default (IAT - SAT) = 20 ºF
RA HTM = - 1.1 x ACF x ALF x (PT - IAT)
Heat Balance for Cooling |  |  |  |  | Sensible |  | For Wrk G |  | For Wrk G1
Floor | Lighting | Ceiling | RA | Sum of | Load |  | Amb DB | Amb DB | Sensible | Latent | Heating
HTM (-) | HTM (+) | HTM (-) | HTM (-) | HTMs | to RA |  | Cooling | Heating | Load | Load | Load
[7 empty] | PT value | PT value | to RA | to RA | to RA
0 | #DIV/0! | 0 | 0 | #DIV/0! | 0 |  | 0 | 70 | 0 | Zero | Zero
The estimated value for plenum temperature (PT) is correct if sum of HTMs = zero (range = ± 1.0).
Sensible cooling load to RA (Btuh) = -RA HTM x FA … i.e, the cooling load is positive.
The return air load is a system load for Form N1, Line 15.
To simplify the heating procedure, the (PT - IAT) effect is ignored (Amb DB PT value equals indoor design temperature from Wroksheet A)..
Note on L19: ALF for load in cell I25

## RAP-3 (hidden)
Worksheet RAP-3
Return Air Plenum Under a Roof and Under a Conditioned Space
|  |  | Type of space load: | Zone | Month | Jul & Aug | Hour | 15:00
Procedure:
1) Determine the floor area for the space under the return air plenum (part of this area will be under a roof and part will be under a conditioned space).
2) Perform RAP-1 heat balance calculations for heating and cooling using the entire floor area of the space covered by the return air plenum.
3) Perform RAP-2 heat balance calculations for heating and cooling using the entire floor area of the space covered by the return air plenum.
4) Determine the floor area for the portion of the space that is under the roof. | [9 empty] | Total floor area = | 0
5) Determine the floor area for the portion of the space that is under a conditioned space. | [9 empty] | Floor area under roof = | 0
6) Use the following forms to calculate the weighted average plenum temperature for cooling and heating. | [9 empty] | Floor area under floor = | 0
7) Use the following form to calculate the weighted average return air loads for cooling and heating.
Average Ambient Temperature for Worksheet G
Weighted average plenum temp for cooling (°F) | [6 empty] | Weighted average plenum temp for heating (°F)
Output | Amb DB | Actual | Total | Average |  |  | Output | Amb DB | Actual | Total | Average
From | Cooling | SqFT | SqFT | Plenum |  |  | From | Heating | SqFT | SqFT | Plenum
| PT value |  |  | Temp °F |  |  |  | PT value |  |  | Temp °F
RAP-1 | 0 | 0 | 0 | #DIV/0! |  |  | RAP-1 | 0 | 0 | 0 | #DIV/0!
RAP-2 | 0 | 0 |  |  |  |  | RAP-2 | 70 | 0
Actual SqFt = floor area under roof for RAP-1 and floor area under conditioned space for RAP-2
Weighted average temperature = (RAP-1 PT x Floor area under roof + RAP-2 PT x Floor area under c-space) / Total floor area
For RAP-2 heating the (PT - IAT) effect is ignored (RAP-2 PT value equals indoor design temperature from Worksheet A).
Average Return Air Loads for Worksheet G1
Weighted average load for sensible cooling (Btuh) | [6 empty] | Weighted average load for heating (Btuh)
Output | Sensible | Actual | Total | Weighted |  |  | Output | Heating | Actual | Total | Weighted
From | Load | SqFT | SqFT | Average |  |  | From | Load | SqFT | SqFT | Average
| to RA |  |  | Load |  |  |  | to RA |  |  | Load
RAP-1 | 0 | 0 | 0 | #DIV/0! |  |  | RAP-1 | 0 | 0 | 0 | #DIV/0!
RAP-2 | 0 | 0 |  |  |  |  | RAP-2 | 0 | 0
Actual SqFt = floor area under roof for RAP-1 and floor area under conditioned space for RAP-2
Weighted average load = (RAP-1 Load x Floor area under roof + RAP-2 Load x Floor area under c-space) / Total floor area
For heating, negative values for the weighted average load default to zero.
Cooling |  |  |  |  | Heating
#DIV/0! | < Avg PT for Wrk G |  |  |  | #DIV/0! | < Avg PT for Wrk G
#DIV/0! | < Avg RA load Wrk G1 |  |  |  | #DIV/0! | < Avg RA load Wrk G1

## Tbl 7-AMB (hidden)
Table 7-AMB |  | Type Load | Month | Hour
Ambient Conditions for Duct Systems |  | Zone | Jul & Aug | 15:00
Location and Attributes |  | Ambient Dry Bulb °F |  | Δ Grains
|  | Heating | Cooling | for Cooling
Outdoors on | Reflective surface in sun | 44 | 108 | 3
Roof or Wall | White or light surface in sun |  | 123
| Dark surface in sun |  | 153
| Any surface in shade or facing North |  | 88
Vented or Unsealed Attic | Unsealed attic or knee wall space that has no vents(construction 16A) | 59 | 143 | 3
| Vented attic with dark, low-mass roof (construction 16B) | 54 | 123
| Vented attic with white, low-mass roof (construction 16C) |  | 113
| Vented attic with dark, high-mass roof (construction 16D) |  | 103
| Vented attic with neutral color, high-mass roof (construction 16E) |  | 98
| Vented attic with white, high-mass roof (construction 16F) |  | 88
Sealed Attic | Any set of attributes listed above. | See Dead Air Cavity
Dead Air | Below a roof (DAC-1) | 0 | 83 | Note 3 | < default > | 1.5
Cavity | Below a conditioned space (DAC-2) | na | 0 | 0
| Cavity below a roof and a conditioned space (DAC-3) | #DIV/0! | #DIV/0! | #DIV/0!
Return Air | Entire return air plenum below a roof (RAP-1) | 0 | 0 | 0
Cavity | Entire return air plenum below a conditioned space (RAP-2) | No load | 0 | 0
| Return air plenum below a roof and a conditioned space (RAP-3) | #DIV/0! | #DIV/0! | 0
Outdoors Below Floor | Open crawlspace or carport or garage | 44 | 88 | 3
Closed Crawlspace | Under and insulated floor, no insulation on crawlspace walls | 50.5 | 84.75 | 3
| No insulation, wall insulation or wall and ceiling insulation | 63.2 | 75
Basement | No insulation, wall insulation or wall and ceiling insulation | 63.2 | 75 | 3
Under Slab | Water proof duct runs under concrete slab | 79 | 75 | 0
Wall Cavity | Riser or drop in wall cavity or chase that has a hostile ambient | 79 | 125.5 | 3
1) OAT = Design value for outdoor dry bulb temperature; Design Gr = Design value for grains difference (for month and hour used for the load estimate)
2) No credit for heat gain from ceiling lighting fixtures; assumes relatively tight ceiling (moisture close to outdoor condition). Use the procedure for a dead
air cavity if lighting gain is significant.
3) This depends on leakage from outdoors and leakage from the conditioned space. Use zero for a tight cavity and a leaky ceiling. Use design Grains for
a leaky cavity and a tight ceiling. Use Design Grains / 2 for a general default.

## Wrk H (hidden)
Worksheet H | [11 empty] | Table 8 Ventilation Rate Evaluation
Ventilation Loads
|  |  | Type of space load: | Zone | Month: | Jul & Aug | Hour: | 15:00 |  |  |  |  | Space | Zone | Month: | Jul & Aug | Hour: | 0.625
Code Value for Outdoor Cfm | [11 empty] | Occupant Activities (Wrk E, Part 2) |  |  |  | Count | CFM / Per | Vent CFM
1) Air changes per hour (ACH) specified by local code: → | [5 empty] | or —> |  |  | Occupants x DF from Worksheet E = | 63 |  | a | Seated, eating a meal |  |  | 52 |  | 0
|  |  |  | Above grade volume CuFt = | 13404 |  | Cfm specified by local code —> |  |  | 460 |  | b | Seated, bar or conference room |  |  | 11 |  | 0
[12 empty] | c | Standing, light work |  |  | 0 |  | 0
Design Cfm Value for Engineered Ventilation | [11 empty] | d | 0 |  |  | 0 |  | 0
2) Code Cfm value |  |  | 689 | < From line 1 above (Cfm = ACH x Volume of Space in Cubic Feet / 60) | [10 empty] | Total Occ = | 63
3) Table 8 Cfm value |  |  | 460 | < This is a default for load estimates (not a standard or good practice recommendation). | [7 empty] | Cfm / Per = 15, 20 or 30, see Table 8 |  |  |  |  | Total Occupant CFM = | 0
4) Space exhaust Cfm |  |  |  | < This relates to makeup air Cfm for air balance (see note 6).
5) Damper leakage Cfm |  |  |  | < Cfm leaking through closed economizer damper or closed outdoor air damper (see note 7). | [7 empty] | Living Spaces |  |  |  | Cfm / Room | No. Rooms | Vent CFM
6) Practitioner-specified VCFM |  |  | 689 | < Consider items 2 through 5 and specify a value that equals or exceeds the damper leakage Cfm. | [7 empty] | Apartments |  |  |  | 30 |  | 0
[12 empty] | Motel or dorm room |  |  |  | 30 |  | 0
Ventilation Loads (evaluated for the month and hour of interest, per outdoor conditions on Worksheet A) | [16 empty] | Total Space CFM = | 0
Type of | VCFM | SER | For Ventilation Dehumidifier |  |  | Outdoor | HTD | T1heat | Indoor | Site | Vent.
Load | or | LER | Condition of |  | Indoor | Condition | and | T1cool | Dry bulb | Elevation | Loads | Applications |  |  |  | CFM / SqFT | SqFt | Vent CFM
| CFMdish | for Heat | Air Leaving |  | Grains | To heat | CTD | DGgrains | T2heat | Feet | (Btuh) | Arcades |  |  |  | 0.3 |  | 0
| (Note 1) | Recovery | Ventilation |  | for Site | To cool | from | for | and | 39 | (Note 5) | Stores and malls |  |  |  | 0.3 |  | 0
|  | Ventilator | Dehumidifier |  | Elevation | ΔGrains | Wks A | entering | T2cool |  |  | Shoping and sales areas |  |  |  | 0.3 |  | 0
|  | (Note 2) | (Note 3) |  | Table 12 | (Wks A) |  | air |  | Table 10A |  | Mall area |  |  |  | 0.2 |  | 0
[8 empty] | (Note 4) |  | ACF |  | Print / Duplicating; Dark room |  |  |  | 0.5 |  | 0
Heating | 689 |  | LATvdh |  |  | 44 | 26 | 44 | 70 | 1 | 19705.4 | Garages |  |  |  | 1.5 |  | 0
Sensible |  |  | LATvdh |  |  | 88 | 13 | 88 | 75 |  | 9852.7 | Locker |  |  |  | 0.5 |  | 0
Latent |  |  | Grainvdh |  |  | 3 |  | 3 |  |  | 1405.56 | Lab animal room |  |  |  | 0.5 |  | 0
[12 empty] | Pet shop or kennel |  |  |  | 1 |  | 0
1) Ventilation Cfm is typically the same for heating and cooling, but two values may be used. For no ventilating dehumidifer, use VCFM from line 4. | [11 empty] | Skating rink |  |  |  | 0.5 |  | 0
| or a ventilation dehumidifier, CFMdish is provided by manufacturer's performance data. | [10 empty] | Wearhouse |  |  |  | 0.15 |  | 0
2) Sensible effectiveness ratings (SERloss, SERgain) and latent effectiveness rating (LER) provided by manufacturer’s engineering data. For | [11 empty] | Swmming pool and deck area |  |  |  | 0.5 |  | 0
| sensible-only equipment, LER = 0. | [10 empty] | Swmming pool spectator area - see Table 8
3) Obtain leaving air temperature (LATVDH) and leaving grains (GrainVDH) from the equipment manufacturer’s engineering data or technical service. | [11 empty] | Toilet room |  |  |  | CFM / Fixture | # Fixtures
4) For outdoor air not processed by a device: T1heat = To heat; T1cool = To cool; DGgrains = DGrains (all from the preceding column). | [15 empty] | 50 |  | 0
For heat recovery: T1heat = To heat + SERheating x HTD; T1cool = To cool - SERcooling x CTD; DGgrains = DGrains x (1.00 - LER) | [16 empty] | Total App. CFM = | 0
For ventilation dehumidifier: T1heat = LATVDH for heating; T1cool = LATVDH for cooling; DGgrains = GrainVDH - Table 12 Grains
5) Heating Load = 1.1 ACF x (VCFM or CFMdish) x (T2heat - T1heat ) | [11 empty] | Default AH Supply Cfm = (Sum of sensible cooling loads on Form N1, Lines 6 through 12) / (20 x ACF)
Sensible Load = 1.1 ACF x (VCFM or CFMdish) x (T1cool - T2cool ) | [14 empty] | Default AH Supply Cfm = | #REF! | < Max damper Cfm for economiser damper.
Latent Load = 0.68 x ACF x (VCFM or CFMdish) x DGgrains | [14 empty] | Measured or specified AH Supply Cfm =
6) If there is no separate source of makeup air, makeup air flows through the outdoor air damper of the air handler that serves the space. The | [14 empty] | Max Cfm through econ damper = | #REF!
practitioner shall decide how much makeup air is required for space pressure control. | [14 empty] | Econ cycle damper provides vent Cfm = |  | < yes = 1
7) Damper leakage Cfm typically ranges between 5% and 10% of the flow through an open damper. If this value is greater than the Cfm required for | [14 empty] | Min OA damper provides vent Cfm = |  | < yes = 1 | < Damper sized for min OA Cfm (or some other less than maxium value)
occupants or makeup air, the damper leakage Cfm establishes the minimum value for VCFM. | [14 empty] | Max Cfm through min OA damper = |  | < Measured or specified
Leakage % for closed damper =
[15 empty] | Damper leakage Cfm for econ damper = | #REF!
[15 empty] | Damper leakage Cfm for min damper = | 0
[15 empty] | Damper leakage Cfm for this scenerio = | err
[15 empty] | Vent Cfm measured in field (or balnk) = |  | < For any type damper at minimum position
[15 empty] | Min OA damper Cfm for this scenerio = | err

## Wrk I (hidden)
Worksheet I
Ancillary Loads
|  |  | Type of space load: | Zone | Month: | Jul & Aug | Hour: | 15:00
Part 1 -- Winter Humidification Heating Load (Btuh)
Enter 2 for winter humid load on line 17, Form N1. Enter 3 for a device that has its own heat source. >
Indoor Conditions |  | Table 1 Values |  | Table | Table 12 Grains |  | Outdoor CFM |  |  | Heating | Gallons
Dry | Relative | Winter | Site | 10A | Outdoor | Indoor | Net Infilt. | Vent. | Total | Load | Per
Bulb | Humidity | Dry-Bulb | Elevation | AC | ODGR | IDGR | NCFM | VCFM | TCFM | (Btuh) | Day
70 | 0% | 44 | 39 | 1 | 0 | 0 | 287.508 | 689 | 976.508 | 0 | 0
Heating Load (Btuh) = 0.68 x ACF x TCFM x (IDGR - ODGR) Gallons Per Day = 0.00272 x Heating Load Add hygroscopic load, if applicable.
Part 2 -- Hot Water, Steam and Chilled Water Piping Load (Btuh)
Pipe Item |  |  | Enter | Feet | Diameter | Fluid | Ambient | Wall TD | Insul. | Pipe | System
Tables 9A1-, 9A-2 |  |  | 1 | of Pipe | (Inches) | Temp. | Temp. | (WTD) | R-Value | Factor | Load
and 9B |  |  | for Bare | (L) |  | (Tf ) °F | Ta °F |  |  | (f) | (Btuh)
|  |  | Pipe | [6 empty] | Table 9
Hot Water or Steam Pipe
a | [7 empty] | 0 |  |  | 0
b | [7 empty] | 0 |  |  | 0
[10 empty] | Total = | 0 | To avoid circular reference problem, fan and pump load-switch cells must be blank, then produce fixed values for current Form N1 space load and equipment load (for 1st run and after each revision).
Chilled Water Pipe
c | [7 empty] | 0 |  |  | 0
d | [7 empty] | 0 |  |  | 0
[10 empty] | Total = | 0
Hot water or steam: WTD = Tf -Ta Chilled water: WTD = Ta -Tf Bare hot pipe: Load = L x f Hot or cold insulated pipe: Load = L x WTD x f
Part 3 -- Blower Motor and Chilled Water Pump Load (Btuh) | [11 empty] | Current
Avoid circular reference problems | [11 empty] | Form N1 Cooling Load
Blower or Pump Heat |  | Blower HP and Motor Efficiency |  |  | Space Load | DT | BT & RA | Pump | Grand Total | Pump | Total Fan | Space | Equipment
Tables 11A and 11B |  | from Manufacturer's |  |  | Line 14b | Load | Load | Head | Load | Load | & Pump | Sensible | Total
DT = Draw Through |  | Table or Field- Measured |  |  | Btuh | for | for | Factor | (Line 21) | Btuh | Load | 40332.0407 | 71665.6536 | < Current load values
BT = Blow Through | [5 empty] | Form N1 | Form N1 | (PHF) | Btuh |  | Form N1 | 40332.0407 | 71665.6536 | < Transcribe current values to these cells
RA = Return Air |  | DT | BT | RA |  | Line 12e | Line 19 | Table 11B |  |  | Line 19 | Use the circular reference procedure after any change to any worksheet.
| Enter 1 if applies | 1 |  | 1 | 40332.0407 | 2016.602 | 1008.301 | Apply = 1 | 71665.6536 | 0 | 1008.301
Fan and Pump Load (Btuh)
| Horse Power | [6 empty] | PHF |  |  |  |  | DT | BT | RA | Pump
| Motor Efficiency > 0; DF = 1.0 | 1 | 1 | 1 | [7 empty] | Actual Value | 0 | 0 | 0 | 0
Default blower power: Supply Fan Load (Btuh) = 0.050 x Block space load = | [5 empty] | 2016.602 | Return Fan (Btuh) = 0.025 x Block space load = |  |  |  | 1008.301 | Default Value | 2016.602 | 2016.602 | 1008.301 | 716.6565
Default Pump Load = 0.0100 x Grand Total Load Default Pump Load for known or estimated head = PHF x Grand Total Load
Actual fan or pump load (Btuh) = 2,545 x Actual shaft HP / Motor efficiency (Efficiency = 1.0 if motor is not in the flow; or DF = 0.95 if in flow.)
Part 4 -- Moisture Migration Load (Btuh) | [12 empty] | Constant fan heat Btuh |  | Constant pump heat
Enter 1 if applied to cooling line 20, Form N1. Enter 2 for winter humid load on line 17, Form N1. Enter 3 for device that has own heat source. > | [12 empty] | DT | BT & RA | Btuh
Description of Construction |  | Const. | Panel | Panel | Irregular | Openings | Gross | Net | Perm | ΔGrains | Latent
Table 13 |  | Number | Length | Width / Hgt | Shape | (SqFt) | Area | Area | Value | Wks A ΔGr | MML |  | For constant fan Cfm or pump Gpm, enter
|  |  | (Ft) | (Ft) | (SqFt) |  | (SqFt) | (SqFt) | Table 13 | 3 | (Btuh) |  | maximum of hourly values.
Exposed Above Grade Wall | [12 empty] | For varable flow fan or pump, leave blank.
a | [6 empty] | 0 | 0 |  |  | 0
b | [6 empty] | 0 | 0 |  |  | 0 |  | For Hour fo Day on Wrk A
c | [6 empty] | 0 | 0 |  |  | 0 |  | Hour fan heat Btuh |  | Hour pump heat Btuh
Partition Walls (for attached garage or any unconditioned space exposed to the outdoor humidity) | [12 empty] | DT | BT & RA
e | [6 empty] | 0 | 0 |  |  | 0 |  | 2016.602 | 1008.301 | 0
f | [6 empty] | 0 | 0 |  |  | 0
Ceilings (vented attic ceiling or any ceiling or roof-ceiling exposed to outdoor humidity)
g | [6 empty] | 0 | 0 |  |  | 0
h | [6 empty] | 0 | 0 |  |  | 0
Ceiling Partitions (any ceiling-partition exposed to outdoor humidity)
i | [6 empty] | 0 | 0 |  |  | 0
j | [6 empty] | 0 | 0 |  |  | 0
Crawlspace Floor – Construction #19 (crawlspace is vented or leaky)
k | [6 empty] | 0 | 0 |  |  | 0
l | [6 empty] | 0 | 0 |  |  | 0
Exposed Floor – Construction #20
m | [6 empty] | 0 | 0 |  |  | 0
n | [6 empty] | 0 | 0 |  |  | 0
MML = (Net Area / 100) x Perm Value x ΔGrains | [9 empty] | Total moisture migration load for Form N1 = | 0