## Slide 1: 6.0 System Documentation & Owner Education (Section 6.1 System Documentation)

## Slide 2: QI Airflow Documentation
Airflow through the heat exchanger
  Field data and calculations recorded on a startup sheet
  Field data and calculations recorded on service records
  Written job documentation or checklist in the installation file

## Slide 3: QI Documentation Required
Documented Field Data recorded on start up sheet
Or
Documented field data recorded on service records
Or
Written job documentation or checklist in the installation file

## Slide 4: Fan Performance Chart ESP & CFM

## Slide 5: Traverse Readings/Measurements
 | a | b | c | d
1 | 340 | 373 | 320 | 394
2 | 366 | 333 | 352 | 391
3 | 362 | 336 | 365 | 331
Airflow measured in feet per minute (fpm) for 8” round duct.
Average value = Total ÷ 12
4263 ÷ 12 = 355 fpm

## Slide 6: Flow Grid Method

## Slide 7: Pressure Matching Method

## Slide 8: Temperature Rise Method

## Slide 9: QI Water Flow Documentation
Water flow through the heat exchanger
  Field data and calculations recorded on a startup sheet
  Field data and calculations recorded on service records
  Written job documentation or checklist in the installation file

## Slide 10: Temperature Rise Method

## Slide 11: Pressure Drop Measurement
Water Pressure Drop (in feet @ 180°F) |  |  | 
GPM | COIL A | COIL B | COIL C
2 | 0.4 | 0.4 | 0.5
4 | 1.4 | 1.6 | 1.7
6 | 3.0 | 3.3 | 3.7
8 | 5.2 | 5.7 | 6.3
10 | 7.9 | 8.7 | 9.6

## Slide 12: Other OEM Approved Methods
50
25
GPM By Head

## Slide 13: Company Start Up Sheet

## Slide 14: QI Refrigerant Charging Methods
Subcooling
Superheat
OEM Approved Methods
  Weigh In
  Temperature Transfer Charts
  Other Methods?

## Slide 15: QI Documentation Required
Documented Field Data recorded on start up sheet
Or
Documented field data recorded on service records
Or
Written job documentation or checklist in the installation file

## Slide 16: OEM Subcooling Chart
87 – 81.4 = 5.6

## Slide 17: OEM Superheat Product Chart

## Slide 18: OEM Charge Listed By Weight

## Slide 19: Line Set Length Adjustment
Additional R-410A Added for Line Length (Weigh In Charge) |  |  | 
Suction Line Size | Ounces per-foot | Liquid Line Size | Ounces per-foot
1/2 | 0.04 | 1/4 | 0.19
5/8 | 0.06 | 5/16 | 0.33
3/4 | 0.09 | 3/8 | 0.51
7/8 | 0.12 | 1/2 | 1.01
1-1/8 | 0.20 | 5/8 | 1.64
Note: generic amounts listed above: use OEM values when available |  |  | 

## Slide 20: Company Start Up Sheet

## Slide 21: Acceptable Electrical & System Controls Documentation
Documents showing that selections are in compliance with OEM specifications
and
Written documentation or checklist in the job file

## Slide 22: Amperage & Voltage Measurements
Compressor
Controls
Motors
Transformers (high and low side)
Heat Strips
Any Part with an OEM rated Amperage

## Slide 23: Compressor Amperage & Voltage
Wire Size and fuse/circuit breaker sizing
meets OEM requirements

## Slide 24: HVAC Safety Switches

## Slide 25: Verify Fuse And Wire Size/Type
Safety Controls
Operating Controls
Motors
Transformers (high and low side)
Heat Strips
Any Part with an OEM rated Amperage/Voltage

## Slide 26: Record AS BUILT Control Wiring

## Slide 27: Company Start Up Sheet

## Slide 28: OEM Manuals

## Slide 29: On-Rate For Combustion Appliances
Gas Appliances:
Clocking the meter
Furnace Temperature Rise
Combustion Analysis Per OEM Directions
Oil Appliances
Verify OEM Compliant Nozzle
Furnace temperature Rise
Combustion Analysis Per OEM Directions

## Slide 30: QI Documentation Required
Documented Field Data recorded on start up sheet
Or
Documented field data recorded on service records
Or
Written job documentation or checklist in the installation file

## Slide 31: Clocking The Gas Meter

## Slide 32: Gas Meter Pressure

## Slide 33: Gas Burner Pressure Check

## Slide 34: Temperature Rise Method
Air Temperature difference between the Warm Air Supply Plenum
and the Return Air Plenum

## Slide 35: Combustion Analysis

## Slide 36: Oil Pump Pressure

## Slide 37: OEM Burner Adjustment Instructions

## Slide 38: Temperature Rise Method
Air Temperature difference between the Warm Air Supply Plenum
and the Return Air Plenum

## Slide 39: OEM Oil Furnace Start Up Sheet

## Slide 40: Distributor/Oem Checklist

## Slide 41: OEM Manuals & Company Start Up Sheet

## Slide 42: QI Approved Duct Leakage Tests
Duct Pressurization Test @ 25 Pascal
Airflow Comparison Method
Hybrid blower door/airflow measuring device subtraction
Duct Pressurization Test meeting AHJ requirements

## Slide 43: QI Documentation Required
Documented Field Data recorded on start up sheet
Or
Documented field data recorded on service records
Or
Written job documentation or checklist in the installation file

## Slide 44: Duct Pressurization

## Slide 45: Airflow Comparison Method

## Slide 46: Hybrid Blower Door/AMD Method

## Slide 47: TAB Report QI Documentation Required
Documented Field Data recorded on start up sheet
Or
Documented field data recorded on service records
Or
Written job documentation or checklist in the installation file

## Slide 48: Air Handler / Furnace Test Report

## Slide 49: Air Handler / Furnace Test Report
X
X
XYZ
XYZ 2345
X
Direct Drive N/A
N/A
N/A
N/A
N/A
1234
1289
1289
1157
N/A
N/A
.12
.12
.12
.45
.45
.45
XYZ
XYZ 1234
1/12
.86
N/A
1157
1157
N/A
N/A
208/230
N/A
211.5
N/A
N/A
N/A
N/A
N/A
N/A

## Slide 50: Air Handler / Furnace Test Report
.12
.12
.12
.45
.45
.45
52/89
77/50
81/51
N/A
.05
.05 wet coil
.30
.008
.008
.50
.42
N/A
.048 wet
.048 wet
.307
.307
N/A
N/A
N/A
N/A
N/A
N/A
N/A
1234
1234
1289
1297
Airflow Test in Cooling Mode Exhaust Fan For 62.2

## Slide 51: Blower Table
P CO Air Resistance Across The Coil |  |  | 
Model Number | Air Volume CFM | Dry Coil in. w.g. | Wet Coil in. w.g.
XYZ | 1200 | 0.03 | 0.04
 | 1400 | 0.08 | 0.09
 | 1600 | 0.14 | 0.17
 | 1800 | 0.22 | 0.29
 | 2000 | 0.31 | 0.42

## Slide 52: Proportional Air Balance
Note:
Proportional
balance work
Sheets are
Available for
Copying in
Manual B and in
the Technician’s
Guide for Quality
Instillations

## Slide 53: Airflow Balance Report
Field data from the balance:

## Slide 54: Hydronic Balancing Reports
A plan can be formulated by gathering and studying the plans, equipment data sheets and making copies of the TAB forms needed

## Slide 55: Pump Curve

## Slide 56: Company Start Up Sheet