## Slide 1: 5.0 Distribution Aspects (Section 5.3 Hydronic Balance)

## Slide 2: Typical Water Supply

## Slide 3: Hydronic Balancing
Ensure water flows meet the design/application
Requirements.

## Slide 4: Diaphragm Expansion Tank

## Slide 5: Expansion of Water
Water Pressure

## Slide 6: Typical Boiler Piping

## Slide 7: System Operating Pressure

## Slide 8: Hydronic System Check
System flushed, filled, and air removed
Water strainers clean
Pump running
Automatic controls open or set
Valves open or set
Maximum required water flow verified

## Slide 9: Acceptable Procedures (For Water Flow)
Water Pressure Drop Method
Or
Water Temperature Change Method
Or
Any method approved and specified by the OEM that can be used to determine water flow rate

## Slide 10: Acceptable Procedures For Pumps
For Pumps the flow is generally found by two methods:
Using the OEM chart for flow based on measuring the head when the discharge valve is closed.
Or
Using a flow measuring Device

## Slide 11: OEM GPM By Head Chart

## Slide 12: Valve Off The Pump Discharge?
0010 Pump
7 PSIG

## Slide 13: PSI to PSIA
7 PSIG
14.7 + PSIG = PSIA
14.7 + 7 = 21.7 PSIA

## Slide 14: PSIA to Feet of Head (h)
7 PSIG or 21.7 PSIA
PSIA X 2.31 ÷ SG = h
21.7 X 2.31 ÷ 1 = 50 h

## Slide 15: Specific Gravity and Viscosity
21.7 X 2.31 ÷ 1 = 50 h

## Slide 16: GPM By Head
50
25

## Slide 17: GPM By Flow Measurement
Triple Duty Balancing Shut Off Valve

## Slide 18: GPM By Flow Measurement
Triple Duty Balancing Shut Off Valve

## Slide 19: GPM By Flow Measurement

## Slide 20: Pump Balancing
GPM by Flow Measurement Balancing Pumps 4.3

## Slide 21: Series-Loop Piping

## Slide 22: 2 Zone Series Loop Piping

## Slide 23: Balancing Valves

## Slide 24: Balancing Valves

## Slide 25: Balancing Valve Chart

## Slide 26
Position 4.5

## Slide 27: Some Valves Have Balancing Calculators/Charts Available

## Slide 28: One-Pipe Using Diverter Ts

## Slide 29: 2 Zone One-Pipe
Balancing Valves

## Slide 30: Two-Pipe System

## Slide 31: 3 Zone Two-Pipe
Balancing Valves
Electronic Zone Valves

## Slide 32: 3 Zone Two-Pipe
Balancing Valves
Electronic Zone Valves

## Slide 33: Pump Laws
(GPMbeginning ÷ GPMfinal) = (RPMbeginning ÷ RPMfinal)
(GPMbeginning ÷ GPMfinal) 2 = (ΔPbeginning ÷ ΔPfinal)
(GPMbeginning ÷ GPMfinal) 3 = (BHPbeginning ÷ BHPfinal)
(GPMnew ÷ GPMold) = (RPMnew ÷ RPMold)
(GPMnew ÷ GPMold) 2 = (ΔPNew ÷ ΔPold)
(GPMnew ÷ GPMold)3 = (BHPnew ÷ BHPold)

## Slide 34: Pump Law 1
GPM, and RPM are proportional and increase at the same rate. A basic TAB principle is faster rotation equals more water moving and it can be expressed in the following equation:
(GPMnew ÷ GPMold) = (RPMnew ÷ RPMold)
Also can be written as:
(GPMnew ÷ GPMold) x RPMold = RPMnew

## Slide 35: Pump Law 1
Example: Calculate the RPM necessary for the pump if the initial speed is 1200 RPM and the original GPM is 10, if the new / required total water flow is 15 GPM.
Formula:
(GPMnew ÷ GPMold) x RPMold = RPMnew
(15 GPM ÷ 10 GPM) x 1200 = RPMnew
Thus:
RPM new = 1.5 x 1200 = 1800 RPM.

## Slide 36: Pump Law 2
A basic TAB principle is that a small increase in GPM will equal a larger increase in ΔP and it is expressed in the following equation:
(GPMNew ÷ GPMOld) 2 = (ΔPNew ÷ ΔPold)
2
=

## Slide 37: Pump Law 2
Example: if the GPM is increased from 10 GPM to 15 GPM and the original ΔP was 8 psig, what will the new ΔP be?
Formula:
(GPMNew ÷ GPMOld)2 = (ΔPNew ÷ ΔPold)
(GPMNew ÷ GPMOld) 2 x ΔPold = ΔPNew
Thus:
ΔPNew= 8 x (15 ÷ 10)2 = 18 psig

## Slide 38: Pump Law 3
A basic TAB principle is that a small increase in GPM will equal a much larger increase in the BHP required to move the increased water flow and this law is expressed in the formula:
(GPMnew ÷ GPMold)3 = (BHPnew ÷ BHPold)
3
=

## Slide 39: Pump Law 3
What BHP is needed to increase GPM from 10 GPM to 15 GPM? If the original BHP was 1/3 BHP, what will the new BHP be?
Formula:
(GPMnew ÷ GPMold)3 = (BHPnew ÷ BHPold)
(GPMnew ÷ GPMold)3 x BHPold = BHPnew
Thus:
BHPnew = .333 x (15 ÷ 10)3 = 1.13 BHP

## Slide 40: Brake Horse Power
BHPsingle phase = (A x V x Eff x PF) ÷ 745.7
Eff = name plate efficiency
PF = name plate power factor
V = measured voltage
A = measured amperage
Note: PF is the work in in Watts divided by the work out in volts multiplied by amps

## Slide 41: Hydronic Balancing Reports
A plan can be formulated by gathering and studying the plans, equipment data sheets and making copies of the TAB forms needed

## Slide 42: Hydronic TAB Reports

## Slide 43: Hydronic TAB Reports
Jones House
123 Pine St Ziplock IL
Don
7 June 201X
whole house heating loop
XZD Co
D578 Circulator
0011
SIF 1100
CI 1100 798G667
Standard / Not Specified
3.1
3250
3250
3.16
12
12.1
XZD Co Direct Drive
N/A
N/A
N/A
N/A
X
N/A

## Slide 44
3.1
32
3250
3.16
32.1
3250
XZD Co Direct Drive
N/A
N/A
N/A
N/A
N/A
X
1/8
1.7
1.68
115
117
3250
N/A
N/A
N/A
N/A
N/A
N/A
N/A
42
10
32
1
32.1
0
32.1
12.1
12.1
0
PUMP AND MOTOR ONE DIRECT DRIVE UNIT

## Slide 45
3.1
32
3250
3.16
32.1
3250
XZD Co Direct Drive
N/A
N/A
N/A
N/A
N/A
X
1/8
1.7
1.68
115
117
3250
N/A
N/A
N/A
N/A
N/A
N/A
N/A
42
10
32
1
32.1
0
32.1
12.1
12.1
0
PUMP AND MOTOR ONE DIRECT DRIVE UNIT

## Slide 46: Hydronic Balancing Reports

## Slide 47: Hydronic Balancing Reports
Jones House
444 Side Street
Don
3 July 14
Hydro-manometer
H-2345
H-2345-1999-201SD
3 Sept. 2013
Boiler 1 - 4 Zone
156 F/30 PSIG
Air found in system needed venting

## Slide 48: Hydronic Balancing Reports
Jones House
444 Side Street
Don
3 July 14
Hydro-manometer
H-2345
H-2345-1999-201SD
3 Sept. 2013
Boiler 1 - 4 Zone
156 F/30 PSIG

## Slide 49: Hydronic Balancing Reports
Jones House
444 Side Street
Don
3 July 14
Hydro-manometer
H-2345
H-2345-1999-201SD
3 Sept. 2013
Boiler 1 - 4 Zone
156 F/30 PSIG
Install Crew Did a Great Job!
Zone 1 Bed Rms
Zone 2 Lv Rm
Zone 3 Kitchen
Zone 4 GR & DR
.80
Totals
.90
.20
1.20
.75
3.10
.91
.25
1.25
3.16
94
101
101
104
102