## Slide 1: Maria’s Restaurant Chapter 3 Section 11

## Slide 2: Duct Design Preparation Steps
Calculate each supply outlet and return inlet’s required CFM based on the Manual N5 (Chapter I) load calculation and the equipment’s airflow capacity (Chapter II).
Sketch the duct blueprint as we expect it will be installed.

## Slide 3: Maria’s Duct Layout Sketch

## Slide 4: OEM Duct Opening Size Chart
28”
20”
24”
27”
Note: Drawing not to scale

## Slide 5: Supply Duct Opening Size Both Zones
Area of OEM Opening in ft2 = ?
ft2 = in2 ÷ 144
(28 × 20) ÷ 144 = 3.89 ft2

## Slide 6: Zone 1 Supply Duct Airflow In FPM
Zone 1 Supply = 2,400 CFM
FPM = CFM ÷ ft2
FPM = 2,400 ÷ 3.89 = 617 FPM

## Slide 7: Zone 1 Supply Duct Airflow In FPM
Zone 2 Supply = 3,200 CFM
FPM = CFM ÷ ft2
FPM = 3,200 ÷ 3.89 = 823 FPM

## Slide 8: Supply Duct Opening Size Both Zones
Find the FPM for Zone 1 and 2 Supply airflow if the duct size was changed to 26” × 24”.
Zone 1:
(26 × 24) ÷ 144 = 4.3333 and 2,400 CFM ÷ 4.3333 = 554 FPM
Zone 2:
(26 × 24) ÷ 144 = 4.3333 and 3,200 CFM ÷ 4.3333 = 739 FPM

## Slide 9: Return Duct Opening Size Both Zones
Area of OEM Opening in ft2 = ?
ft2 = in2 ÷ 144
(27 × 24) ÷ 144 = 4.5 ft2

## Slide 10: Return Duct Airflow FPM Both Zones
Area of OEM Opening in ft2 = ?
FPM = CFM ÷ ft2
Zone 1:
FPM = 2,400 ÷ 4.5 = 533 FPM
Zone 2:
FPM = 3,200 ÷ 4.5 = 711 FPM

## Slide 11: Return Duct Opening Size Both Zones
Find the FPM for Zone 1 and 2 Return airflow if the duct size was changed to 25” × 25”.
Zone 1:
(25 × 25) ÷ 144 = 4.34 and 2,400 CFM ÷ 4.34 = 553 FPM
Zone 2:
(25 × 25) ÷ 144 = 4.34 and 3,200 CFM ÷ 4.34 = 737 FPM

## Slide 12: Friction Rate Calculation
ACCA’s Duct Slide Rule User’s Manual recommends using FR values between 0.08 and 0.20 for the commercial duct sizing procedure.

## Slide 13: Friction Rate Calculation
Friction rate (FR) for 0.2 is translated into CFM for galvanized duct (565 CFM) and Duct Board (410 CFM) duct sizing.

## Slide 14: Friction Rate Calculation 1
Find the CFM corresponding to a FR of 0.045
250 CFM

## Slide 15: Friction Rate Calculation 2
Find the CFM corresponding to a FR of 0.045 for Duct Board
182 CFM

## Slide 16: Friction Rate Calculation 3
Find the FR that provides 310 CFM for Duct Board at this duct size setting.
0.125

## Slide 17: Friction Rate Calculation 4
Find the FR that provides 310 CFM for metal duct at this duct size setting.
0.065

## Slide 18: OEM Supply Duct Opening ½ Blocked
Note: Drawing not to scale

## Slide 19: Field Notes
A common problem found in the field is an immediate reduction in duct size at the equipment inlet and outlet. This is made worse if the reduction is square and not tapered. The author once found a supply duct that was ½ the size of the outlet with the top half just blocked off in the outlet. The call was for no cooling in the building. The duct restriction was causing turbulence in the airflow and a high operating static pressure. The reason the system was not cooling was because the blower motor kept shutting down on an internal overload.