## Slide 1: Technician’s Guide and Workbook for Zoning Section 3: Single Zone Airflow Balancing and Thermostat Location

## Slide 2: Single Zone Airflow Balancing
Balancing is an art based on science. As one does more balancing they become better at balancing and doing the required calculations.
This short lesson on balancing is based on Manual B guidance.

## Slide 3: One Zone For Whole House
Zone 1 2nd Floor
Zone 1 1st Floor

## Slide 4: 1st Floor Manual D CFM Per Diffuser C/H
Dining
Kitchen
Great Room
Garage
½ Bath
Laundry
200/100 CFM
150/100 CFM
140/90 CFM

## Slide 5: 2nd Floor Manual D CFM Per Diffuser C/H
Card Room
&
Bar
Bath
Closet
Bed 2
Bed 3
Bath
Master Bedroom
200/220 CFM
128/130 CFM
120/130 CFM
330/450 CFM

## Slide 6: Single Zone Systems
In our example home there are seven rooms where the thermostat can be placed

## Slide 7: Manual D Design Airflow Totals
Room | Cooling CFM | % Total CFM | Heating CFM | % Total CFM
Kitchen | 200 | 15.8 | 100 | 8.2
GR | 150 | 11.9 | 100 | 8.2
Dining | 140 | 11.0 | 90 | 7.4
Bed 2 | 128 | 10.0 | 130 | 10.7
Bed 3 | 120 | 9.5 | 130 | 10.7
MB | 200 | 15.8 | 220 | 18.0
CR | 330 | 26.0 | 450 | 36.9
Total | 1,268 | 100 | 1,220 | 100.1

## Slide 8: Manual D Design Airflow Totals
Room | Cooling CFM | % Total CFM | Heating CFM | % Total CFM | Test 1 CFM | Design CFM | Final CFM | % of Design
Kitchen | 200 | 15.8 | 100 | 8.2 | 150 |  |  | 
GR | 150 | 11.9 | 100 | 8.2 | 220 |  |  | 
Dining | 140 | 11.0 | 90 | 7.4 | 200 |  |  | 
Bed 2 | 128 | 10.0 | 130 | 10.7 | 150 |  |  | 
Bed 3 | 120 | 9.5 | 130 | 10.7 | 100 |  |  | 
MB | 200 | 15.8 | 220 | 18.0 | 120 |  |  | 
CR | 330 | 26.0 | 450 | 36.9 | 410 |  |  | 
Total | 1,268 | 100 | 1,220 | 100.1 | 1,350 |  |  | 

## Slide 9: Field Airflow Across the Heat Exchanger
Air
Total Measured At Diffusers = 1,350 CFM
Total Measured Across the Heat Exchanger = 1,432
1,350 ÷ 1,432 = 0.9427 = 94%

## Slide 10: Manual D Design Airflow Totals 1
Room | Cooling CFM | % Total CFM | Heating CFM | % Total CFM | Test 1 CFM | % CFM Measured | Final CFM | % of Design
Kitchen | 200 | 15.8 | 100 | 8.2 | 150 |  |  | 
GR | 150 | 11.9 | 100 | 8.2 | 220 |  |  | 
Dining | 140 | 11.0 | 90 | 7.4 | 200 |  |  | 
Bed 2 | 128 | 10.0 | 130 | 10.7 | 150 |  |  | 
Bed 3 | 120 | 9.5 | 130 | 10.7 | 100 |  |  | 
MB | 200 | 15.8 | 220 | 18.0 | 120 |  |  | 
CR | 330 | 26.0 | 450 | 36.9 | 410 |  |  | 
Total | 1,268 | 100 | 1,220 | 100.1 | 1,350 |  |  | 

## Slide 11: Manual D Design Airflow Totals 2
Room | Cooling CFM | % Total CFM | Heating CFM | % Total CFM | Test 1 CFM | Design CFM | Final CFM | % of Design
Kitchen | 200 | 15.8 | 100 | 8.2 | 150 |  |  | 
GR | 150 | 11.9 | 100 | 8.2 | 220 |  |  | 
Dining | 140 | 11.0 | 90 | 7.4 | 200 |  |  | 
Bed 2 | 128 | 10.0 | 130 | 10.7 | 150 | 129 |  | 
Bed 3 | 120 | 9.5 | 130 | 10.7 | 100 |  |  | 
MB | 200 | 15.8 | 220 | 18.0 | 120 |  |  | 
CR | 330 | 26.0 | 450 | 36.9 | 410 |  |  | 
Total | 1,268 | 100 | 1,220 | 100.1 | 1,350 |  |  | 
128 × 0.9 = 115.2 CFM
128 × 1.1 = 140.8 CFM
130 × 0.9 = 117 CFM
130 × 1.1 = 143 CFM

## Slide 12: Manual D Design Airflow Totals 3
Room | Cooling CFM | % Total CFM | Heating CFM | % Total CFM | Test 1 CFM | Design CFM | Final CFM | % of Design
Kitchen | 200 | 15.8 | 100 | 8.2 | 150 |  |  | 
GR | 150 | 11.9 | 100 | 8.2 | 220 |  |  | 
Dining | 140 | 11.0 | 90 | 7.4 | 200 |  |  | 
Bed 2 | 128 | 10.0 | 130 | 10.7 | 150 | 129 |  | 
Bed 3 | 120 | 9.5 | 130 | 10.7 | 100 | 125 |  | 
MB | 200 | 15.8 | 220 | 18.0 | 120 |  |  | 
CR | 330 | 26.0 | 450 | 36.9 | 410 |  |  | 
Total | 1,268 | 100 | 1,220 | 100.1 | 1,350 |  |  | 

## Slide 13: Manual D Design Airflow Totals 3
Room | Cooling CFM | % Total CFM | Heating CFM | % Total CFM | Test 1 CFM | Design CFM | Final CFM | % of Design
Kitchen | 200 | 15.8 | 100 | 8.2 | 150 |  |  | 
GR | 150 | 11.9 | 100 | 8.2 | 220 |  |  | 
Dining | 140 | 11.0 | 90 | 7.4 | 200 |  |  | 
Bed 2 | 128 | 10.0 | 130 | 10.7 | 150 | 129 |  | 
Bed 3 | 120 | 9.5 | 130 | 10.7 | 100 | 125 |  | 
MB | 200 | 15.8 | 220 | 18.0 | 120 | 210 |  | 
CR | 330 | 26.0 | 450 | 36.9 | 410 |  |  | 
Total | 1,268 | 100 | 1,220 | 100.1 | 1,350 |  |  | 

## Slide 14: Manual D Design Airflow Totals 4
Room | Cooling CFM | % Total CFM | Heating CFM | % Total CFM | Test 1 CFM | Design CFM | Final CFM | % of Design
Kitchen | 200 | 15.8 | 100 | 8.2 | 150 |  |  | 
GR | 150 | 11.9 | 100 | 8.2 | 220 |  |  | 
Dining | 140 | 11.0 | 90 | 7.4 | 200 |  |  | 
Bed 2 | 128 | 10.0 | 130 | 10.7 | 150 | 129 |  | 
Bed 3 | 120 | 9.5 | 130 | 10.7 | 100 | 125 |  | 
MB | 200 | 15.8 | 220 | 18.0 | 120 | 210 |  | 
CR | 330 | 26.0 | 450 | 36.9 | 410 |  |  | 
Total | 1,268 | 100 | 1,220 | 100.1 | 1,350 |  |  | 
150 × 0.9 = 135 CFM
150 × 1.1 = 165 CFM
100 × 0.9 = 90 CFM
100 × 1.1 = 110 CFM
150 × 0.8 = 120 CFM
100 × 1.2 = 120 CFM
120

## Slide 15: Manual D Design Airflow Totals 5
Room | Cooling CFM | % Total CFM | Heating CFM | % Total CFM | Test 1 CFM | Design CFM | Final CFM | % of Design
Kitchen | 200 | 15.8 | 100 | 8.2 | 150 |  |  | 
GR | 150 | 11.9 | 100 | 8.2 | 220 | 120 |  | 
Dining | 140 | 11.0 | 90 | 7.4 | 200 |  |  | 
Bed 2 | 128 | 10.0 | 130 | 10.7 | 150 | 129 |  | 
Bed 3 | 120 | 9.5 | 130 | 10.7 | 100 | 125 |  | 
MB | 200 | 15.8 | 220 | 18.0 | 120 | 210 |  | 
CR | 330 | 26.0 | 450 | 36.9 | 410 |  |  | 
Total | 1,268 | 100 | 1,220 | 100.1 | 1,350 |  |  | 
200 × 0.9 = 180 CFM
200 × 1.1 = 220 CFM
100 × 0.9 = 90 CFM
100 × 1.1 = 110 CFM
100 × 1.2 = 120 CFM
200 × 0.8 = 160 CFM
160

## Slide 16: Manual D Design Airflow Totals 6
Room | Cooling CFM | % Total CFM | Heating CFM | % Total CFM | Test 1 CFM | Design CFM | Final CFM | % of Design
Kitchen | 200 | 15.8 | 100 | 8.2 | 150 | 160 |  | 
GR | 150 | 11.9 | 100 | 8.2 | 220 | 120 |  | 
Dining | 140 | 11.0 | 90 | 7.4 | 200 |  |  | 
Bed 2 | 128 | 10.0 | 130 | 10.7 | 150 | 129 |  | 
Bed 3 | 120 | 9.5 | 130 | 10.7 | 100 | 125 |  | 
MB | 200 | 15.8 | 220 | 18.0 | 120 | 210 |  | 
CR | 330 | 26.0 | 450 | 36.9 | 410 |  |  | 
Total | 1,268 | 100 | 1,220 | 100.1 | 1,350 |  |  | 
140 × 0.9 = 126 CFM
140 × 1.1 = 154 CFM
90 × 0.9 = 81 CFM
90 × 1.1 = 99 CFM
90 × 1.2 = 108 CFM
140 × 0.8 = 112 CFM
112

## Slide 17: Manual D Design Airflow Totals 7
Room | Cooling CFM | % Total CFM | Heating CFM | % Total CFM | Test 1 CFM | Design CFM | Final CFM | % of Design
Kitchen | 200 | 15.8 | 100 | 8.2 | 150 | 160 |  | 
GR | 150 | 11.9 | 100 | 8.2 | 220 | 120 |  | 
Dining | 140 | 11.0 | 90 | 7.4 | 200 | 112 |  | 
Bed 2 | 128 | 10.0 | 130 | 10.7 | 150 | 129 |  | 
Bed 3 | 120 | 9.5 | 130 | 10.7 | 100 | 125 |  | 
MB | 200 | 15.8 | 220 | 18.0 | 120 | 210 |  | 
CR | 330 | 26.0 | 450 | 36.9 | 410 |  |  | 
Total | 1,268 | 100 | 1,220 | 100.1 | 1,350 |  |  | 
330 × 0.9 = 297 CFM
330 × 1.1 = 363 CFM
450 × 0.9 = 405 CFM
450 × 1.1 = 495 CFM
494
160 + 120 + 112 + 129 + 125 + 210 = 856
1,350 – 856 = 494
1,350

## Slide 18: Manual D Design Airflow Totals 8
Room | Cooling CFM | % Total CFM | Heating CFM | % Total CFM | Test 1 CFM | Design CFM | Final CFM | % of Design
Kitchen | 200 | 15.8 | 100 | 8.2 | 150 | 160 |  | 
GR | 150 | 11.9 | 100 | 8.2 | 220 | 120 |  | 
Dining | 140 | 11.0 | 90 | 7.4 | 200 | 112 |  | 
Bed 2 | 128 | 10.0 | 130 | 10.7 | 150 | 129 |  | 
Bed 3 | 120 | 9.5 | 130 | 10.7 | 100 | 125 |  | 
MB | 200 | 15.8 | 220 | 18.0 | 120 | 210 |  | 
CR | 330 | 26.0 | 450 | 36.9 | 410 | 494 |  | 
Total | 1,268 | 100 | 1,220 | 100.1 | 1,350 | 1,350 |  | 

## Slide 19: Zr Balancing by Average CFM 1
Room | Cooling CFM | % Total CFM | Heating CFM | % Total CFM | Test 1 CFM | Average CFM | Corrected Average CFM | CFM & % Design
Kitchen | 200 | 15.8 | 100 | 8.2 | 150 | 150 |  | 
GR | 150 | 11.9 | 100 | 8.2 | 220 | 125 |  | 
Dining | 140 | 11.0 | 90 | 7.4 | 200 | 115 |  | 
Bed 2 | 128 | 10.0 | 130 | 10.7 | 150 | 129 |  | 
Bed 3 | 120 | 9.5 | 130 | 10.7 | 100 | 125 |  | 
MB | 200 | 15.8 | 220 | 18.0 | 120 | 210 |  | 
CR | 330 | 26.0 | 450 | 36.9 | 410 | 390 |  | 
Total | 1,268 | 100 | 1,220 | 100.1 | 1,350 | 1,244 |  | 
+
÷ 2 =

## Slide 20: Zr Balancing by Average CFM 2
Room | Cooling CFM | % Total CFM | Heating CFM | % Total CFM | Test 1 CFM | Average CFM | Corrected Average CFM | CFM & % Design
Kitchen | 200 | 15.8 | 100 | 8.2 | 150 | 150 |  | 
GR | 150 | 11.9 | 100 | 8.2 | 220 | 125 |  | 
Dining | 140 | 11.0 | 90 | 7.4 | 200 | 115 |  | 
Bed 2 | 128 | 10.0 | 130 | 10.7 | 150 | 129 |  | 
Bed 3 | 120 | 9.5 | 130 | 10.7 | 100 | 125 |  | 
MB | 200 | 15.8 | 220 | 18.0 | 120 | 210 |  | 
CR | 330 | 26.0 | 450 | 36.9 | 410 | 390 |  | 
Total | 1,268 | 100 | 1,220 | 100.1 | 1,350 | 1,244 |  | 
1,350 ÷ 1,244 = 1.085
1.085 × Average CFM

## Slide 21: Zr Balancing by Average CFM 3
Room | Cooling CFM | % Total CFM | Heating CFM | % Total CFM | Test 1 CFM | Average CFM | Corrected Average CFM | CFM & % Design
Kitchen | 200 | 15.8 | 100 | 8.2 | 150 | 150 | 163 | 
GR | 150 | 11.9 | 100 | 8.2 | 220 | 125 | 136 | 
Dining | 140 | 11.0 | 90 | 7.4 | 200 | 115 | 125 | 
Bed 2 | 128 | 10.0 | 130 | 10.7 | 150 | 129 | 140 | 
Bed 3 | 120 | 9.5 | 130 | 10.7 | 100 | 125 | 136 | 
MB | 200 | 15.8 | 220 | 18.0 | 120 | 210 | 228 | 
CR | 330 | 26.0 | 450 | 36.9 | 410 | 390 | 423 | 
Total | 1,268 | 100 | 1,220 | 100.1 | 1,350 | 1,244 |  | 
1,350 ÷ 1,244 = 1.085
1.085 × Average CFM

## Slide 22: Zr Balancing by Average CFM 4
Room | Cooling CFM | % Total CFM | Heating CFM | % Total CFM | Test 1 CFM | Average CFM | Corrected Average CFM | CFM & % Design
Kitchen | 200 | 15.8 | 100 | 8.2 | 150 | 150 | 163 | 
GR | 150 | 11.9 | 100 | 8.2 | 220 | 125 | 136 | 
Dining | 140 | 11.0 | 90 | 7.4 | 200 | 115 | 125 | 
Bed 2 | 128 | 10.0 | 130 | 10.7 | 150 | 129 | 140 | 
Bed 3 | 120 | 9.5 | 130 | 10.7 | 100 | 125 | 136 | 
MB | 200 | 15.8 | 220 | 18.0 | 120 | 210 | 228 | 
CR | 330 | 26.0 | 450 | 36.9 | 410 | 390 | 423 | 
Total | 1,268 | 100 | 1,220 | 100.1 | 1,350 | 1,244 | 1,351 | 
1,350 ÷ 1,244 = 1.085
1.085 × Average CFM

## Slide 23: Zr Balancing by Average CFM 5
Room | Cooling CFM | % Total CFM | Heating CFM | % Total CFM | Test 1 CFM | Average CFM | Corrected Average CFM | CFM & % Design
Kitchen | 200 | 15.8 | 100 | 8.2 | 150 | 150 | 163 | 
GR | 150 | 11.9 | 100 | 8.2 | 220 | 125 | 136 | 
Dining | 140 | 11.0 | 90 | 7.4 | 200 | 115 | 125 | 
Bed 2 | 128 | 10.0 | 130 | 10.7 | 150 | 129 | 140 | 
Bed 3 | 120 | 9.5 | 130 | 10.7 | 100 | 125 | 136 | 
MB | 200 | 15.8 | 220 | 18.0 | 120 | 210 | 228 | 
CR | 330 | 26.0 | 450 | 36.9 | 410 | 390 | 423 | 
Total | 1,268 | 100 | 1,220 | 100.1 | 1,350 | 1,244 | 1,351 | 

## Slide 24: Zr Balancing by Average CFM 6
Room | Cooling CFM | % Total CFM | Heating CFM | % Total CFM | Test 1 CFM | Average CFM | Corrected Average CFM | CFM & % Design
Kitchen | 200 | 15.8 | 100 | 8.2 | 150 | 150 | 163 | 
GR | 150 | 11.9 | 100 | 8.2 | 220 | 125 | 136 | 
Dining | 140 | 11.0 | 90 | 7.4 | 200 | 115 | 125 | 
Bed 2 | 128 | 10.0 | 130 | 10.7 | 150 | 129 | 140 | 
Bed 3 | 120 | 9.5 | 130 | 10.7 | 100 | 125 | 136 | 
MB | 200 | 15.8 | 220 | 18.0 | 120 | 210 | 228 | 
CR | 330 | 26.0 | 450 | 36.9 | 410 | 390 | 423 | 
Total | 1,268 | 100 | 1,220 | 100.1 | 1,350 | 1,244 | 1,351 | 

## Slide 25: Thermostat Location?
Room | Cooling CFM | % Total CFM | Heating CFM | % Total CFM | Test 1 CFM | Design CFM | Final CFM | % of Design
Kitchen | 200 | 15.8 | 100 | 8.2 | 150 | 160 |  | 
GR | 150 | 11.9 | 100 | 8.2 | 220 | 120 |  | 
Dining | 140 | 11.0 | 90 | 7.4 | 200 | 112 |  | 
Bed 2 | 128 | 10.0 | 130 | 10.7 | 150 | 129 |  | 
Bed 3 | 120 | 9.5 | 130 | 10.7 | 100 | 125 |  | 
MB | 200 | 15.8 | 220 | 18.0 | 120 | 210 |  | 
CR | 330 | 26.0 | 450 | 36.9 | 410 | 494 |  | 
Total | 1,268 | 100 | 1,220 | 100.1 | 1,350 | 1,350 |  | 

## Slide 26: Thermostat Location by C/H Average
Room | Cooling CFM | % Total CFM | Heating CFM | % Total CFM | Design CFM | C/H Ratio | Stat Location | 
Kitchen | 200 | 15.8 | 100 | 8.2 | 160 | 2 |  | 
GR | 150 | 11.9 | 100 | 8.2 | 120 | 1.5 |  | 
Dining | 140 | 11.0 | 90 | 7.4 | 112 | 1.56 |  | 
Bed 2 | 128 | 10.0 | 130 | 10.7 | 129 | 0.98 |  | 
Bed 3 | 120 | 9.5 | 130 | 10.7 | 125 | 0.92 |  | 
MB | 200 | 15.8 | 220 | 18.0 | 210 | 0.91 |  | 
CR | 330 | 26.0 | 450 | 36.9 | 494 | 0.73 |  | 
Total/ Average | 1,268 | 100 | 1,220 | 100.1 | 1,350 | 8.6/1.23 |  | 
Great Room
Bed 2: 1.23 – 0.98 = 0.25
Great Room: 1.5 – 1.23 = 0.27

## Slide 27: Single Zone Systems
In our example home there are seven rooms where the thermostat can be placed.
Plus or minus 15% of the design airflow in a room can result in a 3OF temperature swing.
The worst place to place the thermostat is where the difference between the heating and cooling CFM is the greatest (Kitchen in our example house).

## Slide 28: Design CFM For Balancing
Once the balance is completed, all documentation should be filled in with the final measured CFM values for each room.
If there is a problem room later, those CFM values can be used to make airflow adjustments.
Adjusting one or two rooms in the summer without considering what that will do in the winter will result in messing up the system’s balance.

## Slide 29: Field Notes
Sometimes the homeowners complaint is, “it is always too warm in this room.”
If that is the case, there is probably too much airflow during the heating mode and not enough airflow during the cooling mode.
In some rooms with very high differences between heating and cooling CFM, the room’s balancing damper can be marked with settings for heating and cooling.
Note: those settings for one room could be automated with a single zone damper set with maximum and minimum opening positions (all other rooms need to be tested to make sure they remain proportional for both settings.