## Slide 1: Maria’s Restaurant Chapter 4 Section 14

## Slide 2: Manual T Air Distribution Basics

## Slide 3
Maria’s Restaurant Duct Layout
(one grid square = one ft2)
66 ft.
25 ft.
Zone 1
EX. Hood
Zone 2
Zone 2 Constant Volume 3,200 CFM
Stage 1 Return: 1,300 CFM
Stage 2 Return: 3,100 CFM
Zone 1
Supply Diffuser 550 CFM
5 Supply Diffusers 530 CFM Each
6 Supply Diffusers 400 CFM Each
Zone 1 Constant Volume 2,400 CFM
Return: 1,711 CFM
A
B
C
F
D
E
G
H
A
B
C
D
E
G
F
H

## Slide 4: Supply Diffuser Chart 1

## Slide 5: Noise Criterion Question 1
Based on the table values, what is the preferred noise criterion for selecting diffusers in nonindustrial applications?
NC ˂ 30 the white areas in the chart.

## Slide 6: Noise Criterion Question 1
What is the NC value for a 27×27 diffuser providing 3,650 CFM?
NC ≥ 40 the red area in the chart.

## Slide 7
Maria’s Restaurant Diffuser Throw Zone 1
(one grid square = one ft2)
66 ft.
25 ft.
Zone 1
EX. Hood
Zone 2
Zone 2 Constant Volume 3,200 CFM
Stage 1 Return: 1,300 CFM
Stage 2 Return: 3,100 CFM
Zone 1
Supply Diffuser 550 CFM
5 Supply Diffusers 530 CFM Each
6 Supply Diffusers 400 CFM Each
Zone 1 Constant Volume 2,400 CFM
Return: 1,711 CFM
A
B
C
F
D
E
G
H
A
B
C
D
E
G
F
H

## Slide 8
Maria’s Restaurant Diffuser Throw Zone 2
(one grid square = one ft2)
66 ft.
25 ft.
Zone 1
EX. Hood
Zone 2
Zone 2 Constant Volume 3,200 CFM
Stage 1 Return: 1,300 CFM
Stage 2 Return: 3,100 CFM
Zone 1
Supply Diffuser 550 CFM
5 Supply Diffusers 530 CFM Each
6 Supply Diffusers 400 CFM Each
Zone 1 Constant Volume 2,400 CFM
Return: 1,711 CFM
A
B
C
F
D
E
G
H
A
B
C
D
E
G
F
H

## Slide 9: Diffusers Chart 2

## Slide 10: Supply Diffusers Types

## Slide 11: Supply Diffusers Throw Direction

## Slide 12: Grille Selection Question 1
If a grill was going to be placed in a corner which of the 4 grille types below would you select?
For most locations the third from the left, the corner 2 direction supply register. The single direction diffuser on the left side might be selected for applications where the airflow from the corner all goes in one direction.

## Slide 13: Diffusers Chart Face Velocity 1
What would the face velocity be for a 9×9 Corner diffuser at 0.050 IWC of pressure loss?

## Slide 14: Diffusers Chart Throw 1
What would the throw be in the X & Y directions for a 9×9 corner diffuser at 0.050 IWC of pressure loss?

## Slide 15: Diffusers Chart Ak 1
What would the Ak be for a 12×12 corner diffuser?

## Slide 16: Diffusers Chart Ak 1
What would the CFM be for a 6×6 corner diffuser at 0.020 IWC of pressure loss?

## Slide 17: Diffusers Chart T1
What would the recommended cooling temperature differential for out selected two way diffuser in an 8 foot ceiling application?

## Slide 18: Diffusers Chart T1
450 + 800 ÷ 2 = 625 CFM
What would the recommended CFM for out selected two way diffuser in a 11 foot ceiling application?

## Slide 19: Field Notes
Everything covered in this lesson for supply diffusers is also true for return grilles. They will have identical charts (except for the numbers). In the field it is very common for supply registers to be noisy because they are undersized it is even more common for return grilles to be undersized and noisy. Under sizing also often causes the entire system to have low airflow due to the added pressure drops. Custom or site built supply and return grilles should always be evaluated to see what the pressure drop is and if they are causing a major restriction on the HVAC system. As discussed earlier, a larger blower motor may be needed to generate the higher RPMs needed to overcome the pressure drops across undersized supply diffusers and return grilles. Warning: the resulting increase in noise level may not be welcomed by the customer! The best approach is always to try and increase the diffuser or grill size so it accommodates the design airflows at a reasonable noise level.