## Slide 1: Technician’s Guide and Workbook for Zoning Section 4: Zoning Load Calculations

## Slide 2: Zoning Load Calculations
Load calculations need to be understood by field technicians before they can be successfully implemented.
This section discusses how zones are selected and how they interact at different times of day.

## Slide 3: Load Calculation Basics
First step: a block load for equipment sizing is done so the equipment size can be determined. The equipment selected has expanded data on airflow that is used to determine main duct trunk sizes.
Second step: a load is done for the air distribution components such as branch ducts, zone damper sizing, supply outlet sizing and local auxiliary equipment sizing.

## Slide 4: Block Load
Whole house as one large room.

## Slide 5: Survey or Building Plan Review
When a technician has access to the Manual J load calculation, it is a good practice to review it and make sure it is accurate. For example, if the attic insulation is missing, or if the direction the house is facing is wrong….there may be a problem that needs to be fixed before proceeding with an installation.

## Slide 6: Air Distribution Component Based Load
Duct system sizing used to convert CFM to load.

## Slide 7: Survey or Duct Design Plan Review
When a technician has access to the Duct Design calculation, it is a good practice to review it and make sure it is accurate. For example, make sure the CFM value is equal to or greater than the Manual J value for each room. Make sure all areas on the design are included in the construction plans and parts lists.

## Slide 8: Airflow Design Numbers
Airflow to individual rooms in a Manual J cooling load is rarely equal to airflow for a Manual J heating load. Further, the Manual D duct design is based on the larger of the two Manual J airflow values. To make things slightly more confusing for technicians, the final test and balance design airflow provided to the space is different than every airflow value that was covered previously.

## Slide 9: Airflow Design Comparison

## Slide 10: Totals From The Previous Table
Cooling CFM (A total of 992 CFM when rooms are added together.).
Heating CFM (A total of 880 CFM when rooms are added together.).
Average CFM (A total of 936 CFM when rooms are added together.).
Plus, using the larger of the cooling and heating for duct design would provide a total of 1017 CFM.

## Slide 11: Understanding The Table Calculations
XS H-CFM BC = Excess heating CFM when the system is balanced for cooling (in room 1) using the Manual J design values:
[(116 ÷ 87) – 1] × 100 = 33.3%

## Slide 12: Understanding The Table Calculations
XS C-CFM BH = Excess cooling CFM when the system is balanced for heating (in room 1) using the Manual J design values:
[ (87 ÷ 116) -1] × 100 = -25%

## Slide 13: Understanding The Table Calculations
XS C-CFM BH = Excess cooling CFM when the system is balanced for heating (in room 8) using the Manual J design values:
[ (63 ÷ 75) -1] × 100 = -16%

## Slide 14: Understanding The Table Calculations
XS C-CFM BH = Excess heating CFM when the system is balanced for heating (in room 8) using the Manual J design values:
[ (75 ÷ 63) -1] × 100 = 19%

## Slide 15: Average Approach
The average approach gets us closer to a design value that will offer reasonable comfort for heating and cooling. If the system is balanced for the excess value for heating becomes 16.7% of the design CFM, and for cooling it -12.5% or 12.5% low on airflow. Obviously, one could calculate an airflow value that was slightly lower and get an equal percentage for both values.

## Slide 16: Field Balancing Applications
In the field, the final CFM balancing values would be based on the measured blower CFM value. For example, based on the totaling of our heating and cooling CFM values: cooling calls for 992 CFM and heating calls for 880 CFM. If there is a two-speed blower setting that can come close to satisfying both, a technician would balance for either heating or cooling at the design speed and then double-check-and-make-sure the final airflows for both heating and cooling were within 20% of the balancing design for both modes of operation (heating and cooling / high speed and low speed).

## Slide 17: Using Data For Thermostat Placement
Based on the 8 room/zone values the rooms with the best C÷H ratio can be calculated:
116 ÷ 87 = 1.33
138 ÷ 111 = 1.24
119 ÷ 109 = 1.09
130 ÷ 108 = 1.20
113 ÷ 126 = 0.89
151 ÷ 128 = 1.18
162 ÷ 136 = 1.19
63 ÷ 75 = 0.84

## Slide 18
9 10 11 12 13 14 15 16 17 18 19
Hour of the Day
30,000
25,000
20,000
15,000
10,000
5,000
0
BTUH
1.3 × Average
Average
Block for Total Glass
Block Fenestration Load vs Hour Of the Day

## Slide 19: Zone Fenestration Load vs Hour Of the Day
9 10 11 12 13 14 15 16 17 18 19
Hour of the Day
30,000
25,000
20,000
15,000
10,000
5,000
0
BTUH
1.3 × Average
Average
Block for Total Glass
Zone 1 (N & E)
Zone 2 (S)
Zone 3 (W)

## Slide 20: Everyone Knows When The Sun Is Out

## Slide 21: AED- Adequate Exposure Diversity

## Slide 22: Calculations Using Manual D
Area/zone 1 = 16,551 BTUH
Area/zone 2 = 8,438 BTUH
Area/zone 3 = 16,524 BTUH
Total BTUH for room loads = 41,513
Total BTUH for Block Load = 32,759

## Slide 23: Calculations Using Manual J Zone Branch Values
Area/zone 1 = 19,036 BTUH
Area/zone 2 = 11,684 BTUH
Area/zone 3 = 19,560 BTUH
Total BTUH for room loads = 50,280
Total BTUH for Block Load = 32,759

## Slide 24: What Causes The Difference?
Glass loads are the main cause of the difference between the two loads shown above.
The block load is the sum of the three zone glass loads. For this home’s zones, the block load remains safely below 1.3 times the block average line for the whole day.

## Slide 25: Glass Load Excursions
9 10 11 12 13 14 15 16 17 18 19
Hour of the Day
30,000
25,000
20,000
15,000
10,000
5,000
0
BTUH
1.3 × Average
Average
Block for Total Glass
Zone 1 (N & E)
Zone 2 (S)
Zone 3 (W)
1.3 × Average
Average

## Slide 26: Glass Load Excursions
9 10 11 12 13 14 15 16 17 18 19
Hour of the Day
30,000
25,000
20,000
15,000
10,000
5,000
0
BTUH
1.3 × Average
Average
Block for Total Glass
Zone 2 (S)
Zone 3 (W)
Zone 1 (N & E)
Excursion
Average

## Slide 27: Zoning by Exposure 4-5 PM
9 10 11 12 13 14 15 16 17 18 19
Hour of the Day
4,500
4,000
3,500
3,000
2,500
2,000
1,500
1,000
500
BTUH
East 1
East 2
West 1
West 2
West 3
4-5 PM

## Slide 28: Field Notes
The complaint is simple, this room gets warm in the afternoons in the summer and then, go figure, it gets too warm in the winter in the late afternoon.
If the room has a lot of glass and faces south and/or west it could be the system design did not handle glass load excursions well.
Based on the how warm it gets, adding a window film, or an overhang might resolve the problem. Ask an AC contractor and the answer will usually be an auxiliary unit or zoning. Ask a window contractor….