## Slide 1: Maria’s Restaurant Chapter 2 Section 8

## Slide 2: Cooling Design Information

## Slide 3: Heating Design

## Slide 4: Zone 1 Equipment Selection

## Slide 5: Manual N Zone 1 Heating Load
34,384 Btuh Total Heating Load

## Slide 6: Zone 1 Heating Data Sheet
Zone 1 Heating 7.5 Ton Unit
Design Load 34,384
High Heat Rating 89,000
Low Heat Rating 53,000
89,000 ÷ 34,384 × 100 = 258%
53,000 ÷ 34,384 × 100 = 154%

## Slide 7: Expanded Equipment Heating Data
44OF
34,384 Btuh Total Heating Load
Interpolation for 44OF @ 2,400 CFM is 81,790 Btuh
81,790 ÷ 34,384 × 100 = 238%
From Low Speed OEM Data:
51,600 ÷ 34,384 × 100 = 150%

## Slide 8: Zone 1 Manual N Cooling Load
50,185 Btuh Sensible Cooling Load
21,481 Btuh Latent Cooling Load
71,666 Btuh Total Cooling Load

## Slide 9: Manual N Zone 1 Cooling Load in Tons
71,666 ÷ 12,000 = 5.97

## Slide 10: Zone 1 Cooling Data Sheet
Zone 1 Cooling 7.5 Ton Unit
Design Load 71,666
Gross Load Rating 91,600
Net Load Rating 89,000
91,600 ÷ 71,666 × 100 = 128%
89,000 ÷ 71,666 × 100 = 124%

## Slide 11: 6 Ton Unit Total Cooling Calculations
6-ton unit (same OEM) with a maximum cooling capacity at 2,880 CFM of 78,200 Btuh
78,200 ÷ 71,666 × 100 = 109% of design
Works for Sensible Heat

## Slide 12: 6 Ton Unit Meet 100% Latent Heat?
However, the 6-ton unit cannot meet the latent heat capacity, it only provides 20,500 Btuh for latent heat removal.
The required minimum value is 21,484. Thus, it could only provide 95% of the required moisture removal.
Does not work Latent Heat Load

## Slide 13: Zone 1 Expanded Data
88OF
Design Load @ 2,400 CFM
At 88OF is 71,666 Btuh
Interpolated Load 91,470
91,470 ÷ 71,666 × 100 = 128%

## Slide 14: Latent Load for 7.5 Ton Unit
85OF air entering the outdoor coil, and an entering wet bulb of 67OF at the indoor coil with 2,400 CFM passing through it, the Total capacity in kBtuh is 93.3 kBtuh;
At 95OF the Total capacity in kBtuh is 87.2 (at a 67 OF return WB); thus, our interpolated value for our 88OF design location would be 91.47 kBtuh (see Math Review for interpolation directions).

## Slide 15: Latent Load for 7.5 Ton Unit
In this example, in order to find the latent value we again interpolate using the 80OF dry bulb return air values or simply look at the two values 0.68 and 0.69 and find the value of 0.68 to be close enough.
Based on table values, at full capacity our sensible cooling ÷ total cooling = 0.68 so, 0.68 × 91,470 Btuh = sensible heat = 62,199.6 or 62,200 Btuh. Thus, the latent cooling capacity must be 93,300 – 62,200 = 31,100 Btuh ( more than 21,382).
Works for Latent Heat

## Slide 16: Manual CS Mild Climate Sizing Limits
Sensible capacity exceeds sensible load.
Latent capacity exceeds latent load.
X Total capacity less than 1.15 × Total Load
1.15 × 71,666 = 82,416 (6.87 tons max size)
Note for multi speed compressor units 0.90 to 1.20 × Total Load
89,000 ÷ 71,666 × 100 = 124%

## Slide 17: OEM 6 Ton to 7.5 Ton Sizing Gap
CS: Total capacity less than 1.15 × Total Load
(Note: for multi speed compressor units 0.90 to 1.20 × Total Load)
OEM expanded data for high speed:
89,000 ÷ 71,666 × 100 = 124%
Options if AHJ won’t allow the slight oversizing:
Variable compressor speed for 0.90 to 1.30 × Total Load.
Another brand that has a 7 ton rooftop unit.
Two smaller systems

## Slide 18: Table 9B

## Slide 19: Table 9B Question 1
Using Table 9B on Page 37 in Maria’s Restaurant Guide & Workbook, find the total cooling capacity in Btuh for the XHP 7.5-86Z in operating in low speed on an 85OF outdoor temperature, and with a return air wet bulb temperature of 67OF and a fan CFM of 3,000.

## Slide 20: Table 9B Question 1
For an outdoor temperature of 85OF the capacity is 48,700 Btuh and for an outdoor temperature of 95OF it is 45,300 Btuh. Note: kBtuh means 1,000 Btuh so the 48.7 is multiplied by 1,000 to get Btuh.

## Slide 21: Table 9B Question 2
Using Table 9B on Page 37 in Maria’s Restaurant Guide & Workbook, find the total latent capacity in Btuh for the XHP 7.5-86Z in operating in low speed with a return air wet bulb temperature of 67OF on an 85OF day, with a fan CFM of 3,000 and a 75 OF outdoor dry bulb temperature.

## Slide 22: Table 9B Question 2
From the chart: at 85OF the sensible over total heat ratio is 0.51 thus, with a total capacity of 48,700 Btuh our sensible capacity would be 48,700 × 0.51 = 24,837
Note: to double check simply divide 24,837 by 0.51 and make sure it equals 48,700 .
Thus, the latent capacity would be 48,700 – 24,873 = 23,827 Btuh

## Slide 23: Table 9B Question 3
Find the sensible if the latent heat is 42,840 and the total capacity is 126,000.

## Slide 24: Table 9B Question 3
The total minus the latent equals the sensible. Thus, 126,000 – 42,840 = 83,160 Btuh
Note: 126,000 × 0.66 = 83,160 Btuh

## Slide 25: Table 9C Question 1
Using Table 9C on Page 38 in Maria’s Restaurant Guide & Workbook, find the total latent capacity in Btuh for the XHP 10-86Z in operating in high speed with a return air wet bulb temperature of 67OF and a fan CFM of 3,200 with a 85OF outdoor dry bulb temperature.

## Slide 26: Table 9C Question 1
From the chart: at 3,200 CFM & 80OF Dry Bulb the sensible over total heat ratio is 0.66 thus, with a total capacity of 126,600 Btuh our latent capacity would be 126,600 × (1 - 0.66) = 43,044 Note: Took a short cut, the previous method works for this example too.

## Slide 27: Table 9C Question 2
Find the sensible heat for the previous example where the latent heat is 43,044 and the total capacity is 126,600.

## Slide 28: Table 9C Question 2 Answer
The total minus the latent equals the sensible. Thus, 126,600 – 43,044 = 83,556 Btuh
Alternate approach: 126,600 × 0.66 = 83,556 Btuh

## Slide 29: Field Notes
Changing fan speed and thus, the CFM changes the performance of the commercial equipment. This often happens when a pulley position is changed so the wrong size belt can be put on to get it running. The change in performance may then become the cause of many call backs and the change does not get caught.