## Slide 1: Maria’s Restaurant Lesson 18 Appendix A Zone 2 Equipment Loads

## Slide 2
Maria’s Restaurant Design
(Staff: Maria & 7 Employees each shift. Glass Store Front and front door)
66 ft.
25 ft.
F1
R1
S1
DW
C1
CT/O
C2
C3
SP
Fry
R2
F2
Woman’s
Restroom
1 handicap
1 standard
Men’s
Restroom
1 handicap
1 urinal
H1
Bar
Ice
C6
Counter
S3
C7
Bar 12 X 10
Seating 12
Restaurant 33 X 15
11 X 4 & 11 X 6
Seating 58
R3
R4
B1
Shelv.
S2
SK
B = Beverage Area R = Refrigerator (blue walk in
C = Counter S = Sink; S1 Hand; S2 3 Pot; S3 Bar
CT = 4 burner plus flat top over ovens SK= Steam Kettle
DW = Dishwasher SP = Salad/cold Prep table
F = Freezer (blue walk in) H1 = Hot Prep Table with Heat Lamp Shelf
Shelv..
Shelving/Storage
WH
S1
B2
Zone 2

## Slide 3: Kitchen and Dish Area Equipment
For Maria’s Restaurant, the kitchen area equipment’s total Btuh value is: 57,732 Btuh
The following presentation shows how the total Btuh was calculated for each piece of equipment shown on the drawing, and then added to some small appliances not shown on the drawing Maria has specified electrical circuits for.

## Slide 4: Restaurant Sandwich/Salad Prep Refrigerator
Manual N Table 6E
Cold Storage Equipment
Refrigerator, 5 to 25 CuFt
Rated Capacity Default Value
1,670 Btuh per 10 Cu Ft (no Hood)
9.75 ÷ 10 x 1,670 = 1,628 Btuh

## Slide 5
2 Hand Wash Sinks
No appreciable Btuh

## Slide 6: Tankless Hot Water Heater
No appreciable Btuh

## Slide 7
3 Pot Sink
No appreciable Btuh

## Slide 8
Gas Steam Kettle
100,000 BTU/hr, 20 Gallon
32.7” wide
Manual N Table 6E
Steam Kettle, large (80 to 320 quarts); With Hood: 32 Btuh per quart
20 x 4 = 80 Qt
80 x 32 = 2,560 Btuh

## Slide 9: Steam Kettle Question
Based on Manual N Table 6E that states: steam table 80 to 320 quarts with hood 32 Btuh per quart.
Find Btuh for a 300 quart steam kettle.
300 × 32 = 9,600 Btuh

## Slide 10: Gas Range Griddle-Oven
Manual N Table 6E
2 Gas Convection Ovens, full size
With Hood:
5,700 Btuh each = 11,400 Btuh

## Slide 11: Gas Range Griddle-Oven
Manual N Table 6E
Gas Oven top, open burner, 2 to 6 burners
Per 2 burner section With Hood:
2,200 Btuh each = 4,400 Btuh

## Slide 12: Gas Range Griddle-Oven
Manual N Table 6E
Gas Oven Top, hot top or fry top
(2 to 6 feet) per linear foot With Hood:
3,100 Btuh each
3.0967 linear feet x 3,100 = 9,600 Btuh

## Slide 13: 2 Gas Deep Fat Fryers
43 lb Oil Capacity
Manual N Table 6E
Fryer, Gas, exhaust hood required
Deep fat (35-50 lbs):
1,900 Btuh each
2 fryers = 3,800 Btuh

## Slide 14: Find The Total Load For The Following:
All equipment under a hood:
Manual N Table 6E
4 Gas Convection Ovens, full size 5,700 Btuh each.
4 Gas 4 open burner Oven tops, open burner, 2 to 6 burners Per 2 burner section 2,200 Btuh each.
3 Fryer, Gas, Deep fat (35-50 lbs.): 1,900 Btuh each.

## Slide 15: Find The Total Load For The Following:
All equipment under a hood:
Manual N Table 6E
4 Gas Convection Ovens, full size 5,700 Btuh each.
4 × 5,700 = 22,800
4 Gas 4 open burner Oven tops, open burner, 2 to 6 burners Per 2 burner section 2,200 Btuh each.
3 Fryer, Gas, Deep fat (35-50 lbs.): 1,900 Btuh each.

## Slide 16: Find The Total Load For The Following:
All equipment under a hood:
Manual N Table 6E
4 Gas Convection Ovens, full size 5,700 Btuh each.
4 × 5,700 = 22,800
4 Gas 4 open burner Oven tops, open burner, 2 to 6 burners Per 2 burner section 2,200 Btuh each.
8 × 2,200 = 17,600
3 Fryer, Gas, Deep fat (35-50 lbs.): 1,900 Btuh each.

## Slide 17: Find The Total Load For The Following:
All equipment under a hood:
Manual N Table 6E
4 Gas Convection Ovens, full size 5,700 Btuh each.
4 × 5,700 = 22,800
4 Gas 4 open burner Oven tops, open burner, 2 to 6 burners Per 2 burner section 2,200 Btuh each.
8 × 2,200 = 17,6--
3 Fryer, Gas, Deep fat (35-50 lbs.): 1,900 Btuh each.
3 × 1,900 = 5,700
22,800 + 17,600 + 5,700 = 46,100 Btuh

## Slide 18: Exhaust Hood
11’ 6” No appreciable Btuh

## Slide 19: Dishwasher
From OEM data with Direct Vent:
4,600 + 6,000 = 10,600 Btuh Total Heat

## Slide 20: OEM Table Question
Based on the OEM Table above what is the total load if the system does not have a direct vent?
13,000 + 5,600 = 18,600 Btuh

## Slide 21: Sink, Disposal and Grease Trap
No appreciable Btuh

## Slide 22: Walk in Cooler
Remote Rooftop Condenser
No appreciable Btuh

## Slide 23: Walk in Freezer
Remote Rooftop Condenser
No appreciable Btuh

## Slide 24: 1 Prep Refrigerator
Manual N Table 6E
Refrigerator 25 to 75 Cu.ft.: per 10 Cu.ft. of space 753
Rated at 49 Cuft;
49 ÷ 10 = 4.9 Thus; 4.9 x 753 = 3,690 Btuh

## Slide 25: 1 Prep Freezer Unit
Note: Thus, the math in N is verified!
(3,778 Btuh for the freezer application is slightly
larger than the 3,690 Btuh for the same unit
used for a refrigeration application.)
Manual N Table 6E
Freezer 18 Cuft 2,760 Btuh
Freezer 73 Cuft 4,570 Btuh
Interpolated value for 49 Cuft:
Approximately 3,778 Btuh

## Slide 26: Prep Tables
No appreciable Btuh

## Slide 27: Electric Steam Table
Electric Steam Table With 2 800w Heat lamp serving station on pick up shelves over it.
Manual N Table 6E
Food Warmer; well type, 0.7 to 2.5 Cuft; 3,620 Btuh
per cuft of Capacity: Not a good fit
Let’s use watts and include the lamps:
Unit 1,920 Watts, Lamp 800 Watts
1,920 + 800 + 800 = 3,520 Watts
1 Watt = 3.412 Btu, Thus:
3.412 X 3,520 = 12,010 Btuh

## Slide 28: Small Kitchen & Dish Area Equipment
Manual N Table 6E, All without hood in Btuh:
(sensible + latent where applicable)
Toaster small conveyor = 1,900 + 1,600 = 3,500
Blender 1-4 Qt = 1,000 + 520 = 1,520
Can Opener = 580
Food Processor 2-3 Qt = 1,770 Btuh
Mixer Small per Qt Capacity 8 Qt @ 48 = 384 Btuh
Total Small Appliance in Kitchen Load = 7,754 Btuh

## Slide 29: Kitchen Area Equipment Cooling Load (Sensible + Latent where applicable)
Refrigeration/Freezer: 3,690 + 3,778 7,468 Btuh
Dish Washer: 4,600 + 6,000 10,600 Btuh
Steam Kettle: 1,280 + 1,280 2,560 Btuh
Two Cook Tops: 16,100 Btuh
Convection Ovens: 11,400 Btuh
Fryers: 3,800 Btuh
Salad Prep Refrigeration: 814 +814 1,628 Btuh
Hot Serve Table: 9,704 + 2,306 12,010 Btuh
Small Appliances: 5,634 +2,120: 7,754 Btuh
Kitchen Equipment Total: 73,320 Btuh
Total Latent Load: 16,298 Btuh

## Slide 30: Zone 2 Speedsheet

## Slide 31: Internal Loads Equipment
Diversity Factor:
Fraction of active or powered units
For internal gains.

## Slide 32: Food Service Equipment Internal Load
Food Service Equipment Load =
73,320 + 16,298 = 89,618 Btuh
Total Internal Load = DF × 89,618 Btuh
Total Internal Load = 0.5 × 89,618 = 44,809 Btuh

## Slide 33: Diversity Factor Question
Food Service Equipment Load =
73,320 + 16,298 = 89,618 Btuh
Total Internal Load = DF × 89,618 Btuh
What would the total load be if the DF was 0.66?
Total Internal Load = 0.66 × 89,618 = 59148 Btuh

## Slide 34: Zone 2 Manual N Summary

## Slide 35: Field Notes
A kitchen was always hot and humid. The technician was called to check the HVAC system. While there, the technician noticed the exhaust venting over the dishwasher didn’t seem to be removing moisture and heat intermittently. After making sure the HVAC system was operating as designed, the technician checked the exhaust fan for the dishwasher vent and found the single-phase exhaust motor was running at high amps (at the correct voltage) and was going off on an internal overload intermittently. Thus, it was determined the motor was undersized. The ¾ HP motor was replace with a 1 HP motor and the hood stayed on. This resolved the cooling issue in the kitchen. Note: the calculated heat load increase from the vented to the unvented dishwasher example shown in this lesson could be calculated as 18,600 – 10,600 = 8,000 Btuh, and all of that increase is in latent heat.